## WI western Yuha Route
Evaporation Losses from Canal
Canal width | 30 | ft
Canal apex elevation | 305 | ft
Canal depth | 12 | ft
Canal exposed length | 150 | miles
Canal exposed length | 792000 | ft
Canal capacity | 54000 | AF
Avg Annual Precipitation Inflow Rate | 7.5 | AF/yr
Avg Annual Evaporation Rate | 68 | in/yr
Net Avg Annual Canal Balance | -25492.5 | AF/yr
Avg Daily Flow Rate | -78.4385 | AF/day
constant | 325851 | gal/AF
Flow Rate (gpm) | -17749.48 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | -1.1198 | cu-m/s
Sea Water Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Head Pressure | 305 | ft
Head Pressure | 92.964 | m
Archimedes Screw Turbine Efficiency | 85%
Power from Water | -885126.168 | Watts
Peak Flow Rate | -1.1198 | cu-m/s
Hours per day | 24 | hr
Daily Flow Rate | -78.4385 | AF/day
System Availability | 0.95
Power Sales Rate | 0.1 | $/kWh
Revenue loss while evaporating | -88.5126 | $/hr
Annual Hydro Power Evaporation Loss | -736601.997 | $/yr
Pump Up Calculation
Daily Seawater Pump Up Rate | 2800 | AF/day
Seawater Salinity Sea of Cortez | 37000 | ppm TDS
Annual Seawater Pump Up Rate | 910000 | AF/yr
constant | 325851 | gal/AF
Pumping Hours per day | 24 | hr
Pump Up Flow Rate | 633599.1667 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | 39.9742 | cu-m/s
Seawater Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Pump Head | 305 | ft
Pump Head | 92.964 | m
Archimedes Screw Pump Efficiency | 85% | %
Generator Efficiency | 92%
Gearbox Efficiency | 97%
Net Efficiency | 75.85%
Power to Lift Water | 49004586.817 | Watts
Power to Lift Water | 49.0046 | MW
Pump Up Power Rate | 0.1 | $/kWh
Cost to Lift Water | 4900.4587 | $/hr
Annual Power Cost to Lift Seawater | 42928018.0517 | $/yr
Energy Recovery Calculation
Drop for canal flow | 52.5 | ft
Annual Hydro Recovery Rate | 884507.5 | AF/yr
Avg Daily Hydro Recovery Rate | 2721.5615 | AF/day | 993369.9615
constant | 325853.3837 | gal/AF
Canal Flow Rate (gpm) | 615854.1918 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | 38.8544 | cu-m/s
Seawater Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Head Pressure | 491 | ft
Head Pressure | 149.6568 | m
Archimedes Screw Turbine Efficiency | 85%
Generator Efficiency | 92%
Gearbox Efficiency | 97%
Net Efficiency | 75.85%
Power from Water | 44119998.2625 | Watts
Power from Water | 44.12 | MW
Peak Flow Rate | 34.6736 | cu-m/s
Operating Hours per day | 24 | hr
Daily Flow Rate | 2428.7215 | AF/day
System Availability | 95%
Power Rate | 0.085 | $/kWh
Revenue while running | 3750.1999 | $/hr
Annual Hydro Recovery Revenue | 31209163.1709 | $/yr
Net Power Output | -4.8846 | MW
Cost and Revenue Calculation
Unit Cost of Turbine Generators | 2400 | $/kW
Capital Cost of Turbine Generators | 105887995.83 | $
Life of Turbine Generators | 25 | yrs
O&M Cost of Turbine Generators | 100 | $/kW
Amortized Cost of Turbine Generators | 4235619.8332 | $/yr
Cost of Spillways | 1000 | $/kW
Capital Cost of Spillways | 44119998.2625 | $
Life of Spillways | 50 | yrs
O&M Cost of Spillways | 3 | $/kW
Amortized Cost of Spillways | 882402.9652 | $/yr
Cost of Power Transmission | 1.69 | $/kW-month
Cost of Power Transmission | 0.0023472 | $/kWh
Annual Cost of Power Transmission | 894753.5648 | $/yr
Unit Cost of Pump Screws | 2400 | $/kW
Capital Cost of Pump Screws | 117611008.3608 | $
Life of Pump Screws | 25 | yrs
O&M Cost of Pump Screws | 100 | $/kW
Amortized Cost of Pump Screws | 4704540.3344 | $/yr
Unit Cost of Seawater Pump Motors | 1000 | $/kGPM
Capital Cost of Seawater Pump Motors | 615854.1918 | $
Life of Seawater Pump Motor | 15 | yrs
O&M Cost of Seawater Pump Motors | 100 | $/kGPM
Amortized Cost of Seawater Pump Motors | 41156.9461 | $/yr
Total Annual Cost | 10758473.6438 | $/yr
Net Revenue | -23213930.5215 | $/yr
Total Capital Cost (pumps,turbines) | 268234856.6451

## WI eastern New River Route
Evaporation Losses from Canal
Canal width | 30 | ft
Canal apex elevation | 185 | ft
Canal depth | 12 | ft
Canal exposed length | 167 | miles
Canal exposed length | 881760 | ft
Canal capacity | 60120 | AF
Avg Annual Precipitation Inflow Rate | 7.5 | AF/yr
Avg Annual Evaporation Rate | 68 | in/yr
Net Avg Annual Canal Balance | -28382.5 | AF/yr
Avg Daily Flow Rate | -87.3308 | AF/day
constant | 325851 | gal/AF
Flow Rate (gpm) | -19761.6795 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | -1.2468 | cu-m/s
Sea Water Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Head Pressure | 185 | ft
Head Pressure | 56.388 | m
Archimedes Screw Turbine Efficiency | 85%
Power from Water | -597744.0862 | Watts
Peak Flow Rate | -1.2468 | cu-m/s
Hours per day | 24 | hr
Daily Flow Rate | -87.3308 | AF/day
System Availability | 0.95
Power Sales Rate | 0.1 | $/kWh
Revenue loss while evaporating | -59.7744 | $/hr
Annual Hydro Power Evaporation Loss | -497442.6285 | $/yr
Pump Up Calculation
Daily Seawater Pump Up Rate | 2800 | AF/day
Seawater Salinity Sea of Cortez | 37000 | ppm TDS
Annual Seawater Pump Up Rate | 910000 | AF/yr
constant | 325851 | gal/AF
Pumping Hours per day | 24 | hr
Pump Up Flow Rate | 633599.1667 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | 39.9742 | cu-m/s
Seawater Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Pump Head | 185 | ft
Pump Head | 56.388 | m
Archimedes Screw Pump Efficiency | 85% | %
Generator Efficiency | 92%
Gearbox Efficiency | 97%
Net Efficiency | 75.85%
Power to Lift Water | 29724093.6431 | Watts
Power to Lift Water | 29.7241 | MW
Pump Up Power Rate | 0.1 | $/kWh
Cost to Lift Water | 2972.4094 | $/hr
Annual Power Cost to Lift Seawater | 26038306.0314 | $/yr
Energy Recovery Calculation
Drop for canal flow | 66 | ft
Annual Hydro Recovery Rate | 881617.5 | AF/yr
Avg Daily Hydro Recovery Rate | 2712.6692 | AF/day | 990124.2692
constant | 325853.3837 | gal/AF
Canal Flow Rate (gpm) | 613841.9776 | gpm
constant | 1233.489 | cu-m/AF
Flow Rate | 38.7274 | cu-m/s
Seawater Density | 1020 | kg/cu-m
Acceleration of gravity | 9.8066 | m/sq-s
Head Pressure | 357.5 | ft
Head Pressure | 108.966 | m
Archimedes Screw Turbine Efficiency | 85%
Generator Efficiency | 92%
Gearbox Efficiency | 97%
Net Efficiency | 75.85%
Power from Water | 32019070.7072 | Watts
Power from Water | 32.0191 | MW
Peak Flow Rate | 34.5603 | cu-m/s
Operating Hours per day | 24 | hr
Daily Flow Rate | 2420.786 | AF/day
System Availability | 95%
Power Rate | 0.085 | $/kWh
Revenue while running | 2721.621 | $/hr
Annual Hydro Recovery Revenue | 22649330.0462 | $/yr
Net Power Output | 2.295 | MW
Cost and Revenue Calculation
Unit Cost of Turbine Generators | 2400 | $/kW
Capital Cost of Turbine Generators | 76845769.6973 | $
Life of Turbine Generators | 25 | yrs
O&M Cost of Turbine Generators | 100 | $/kW
Amortized Cost of Turbine Generators | 3073930.7879 | $/yr
Cost of Spillways | 1000 | $/kW
Capital Cost of Spillways | 32019070.7072 | $
Life of Spillways | 50 | yrs
O&M Cost of Spillways | 3 | $/kW
Amortized Cost of Spillways | 640384.4141 | $/yr
Cost of Power Transmission | 1.69 | $/kW-month
Cost of Power Transmission | 0.0023472 | $/kWh
Annual Cost of Power Transmission | 649346.7539 | $/yr
Unit Cost of Pump Screws | 2400 | $/kW
Capital Cost of Pump Screws | 71337824.7434 | $
Life of Pump Screws | 25 | yrs
O&M Cost of Pump Screws | 100 | $/kW
Amortized Cost of Pump Screws | 2853612.9897 | $/yr
Unit Cost of Seawater Pump Motors | 1000 | $/kGPM
Capital Cost of Seawater Pump Motors | 613841.9776 | $
Life of Seawater Pump Motor | 15 | yrs
O&M Cost of Seawater Pump Motors | 100 | $/kGPM
Amortized Cost of Seawater Pump Motors | 41022.7985 | $/yr
Total Annual Cost | 7258297.7442 | $/yr
Net Revenue | -11144716.3579 | $/yr
Total Capital Cost (pumps,turbines) | 180816507.1255