## Financials 20 MGD VTE, SGSP
Salton Sea, Water Import Salt Extraction Revenue

## Annnual Cost & Revenue 20 MGD
Year | Inflation | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077
Management Team |  | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000 | 936000
Management Expenses |  | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160 | 97160
Engineering Team |  | 1313000 | 1313000 | 1313000 | 1313000 | 1313000 | 1313000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Engineering Support |  | 25000 | 25000 | 25000 | 25000 | 25000 | 25000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Subtotal |  | 2371160 | 2371160 | 2371160 | 2371160 | 2371160 | 2371160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160 | 1033160
Seawater Import cost (long term contract with US & Mexico)
Quantity of seawater imported (acre feet per year) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000 | 900000
Imported seawater commodity purchase from Mexico | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000 | 54000000
Imported seawater conveyance purchase from State or U.S. Federal | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000 | 40500000
Purified salt & water production from Geothermal Distillation
Number of 6 MGD Salt Separation Plants in Design/Permitting |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of 6 MGD Salt Separation Plants in Construction |  | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of 6 MGD Salt Separation Plants in Operation |  | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
6 MGD Salt Separation Plants Capital Cost |  | 0 | 0 | 16500000 | 16500000 | 16500000 | 16500000 | 16500000 | 16500000 | 16500000 | 16500000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 MGD Salt Separation Plants Operating Cost |  | 0 | 0 | 0 | 1894484.9344 | 3788969.8688 | 5683454.8032 | 7577939.7376 | 9472424.672 | 11366909.6064 | 13261394.5408 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752 | 15155879.4752
6 MGD Salt Separation Plants Energy Cost (paid to geothermal) |  | 0 | 0 | 0 | 778107 | 1556214 | 2334321 | 3112428 | 3890535 | 4668642 | 5446749 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856 | 6224856
Pecentage of Purified Salt sent to Vacuum Refining |  | 0% | 0% | 0% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52% | 54.52%
Metric Tons of Solar Salt Produced |  | 0 | 0 | 0 | 72323.2622 | 144646.5243 | 216969.7865 | 289293.0486 | 361616.3108 | 433939.573 | 506262.8351 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973 | 578586.0973
Salt Evaporation Ponds Capital Cost |  | 0 | 0 | 453744.165 | 453744.165 | 453744.165 | 453744.165 | 453744.165 | 453744.165 | 453744.165 | 453744.165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Salt Evaporation Ponds Operating Cost |  | 0 | 0 | 0 | 28103.6415 | 56207.283 | 84310.9246 | 112414.5661 | 140518.2076 | 168621.8491 | 196725.4907 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322 | 224829.1322
Land covered with solar salt evaporation ponds (acres) |  | 0 | 0 | 0 | 16.4349 | 32.8698 | 49.3046 | 65.7395 | 82.1744 | 98.6093 | 115.0441 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479 | 131.479
Price of Solar Salt (2017 USGS trendline price per metric tonne) | 2.1 | 90 | 92.1 | 94.2 | 96.3 | 98.4 | 100.5 | 102.6 | 104.7 | 106.8 | 108.9 | 111 | 113.1 | 115.2 | 117.3 | 119.4 | 121.5 | 123.6 | 125.7 | 127.8 | 129.9 | 132 | 134.1 | 136.2 | 138.3 | 140.4 | 142.5 | 144.6 | 146.7 | 148.8 | 150.9 | 153 | 155.1 | 157.2 | 159.3 | 161.4 | 163.5 | 165.6 | 167.7 | 169.8 | 171.9 | 174 | 176.1 | 178.2 | 180.3 | 182.4 | 184.5 | 186.6 | 188.7 | 190.8 | 192.9 | 195 | 197.1 | 199.2 | 201.3 | 203.4 | 205.5 | 207.6 | 209.7
Annual Revenue from Solar Salt |  | 0 | 0 | 0 | 6964730.146 | 14233217.9931 | 21805463.5413 | 29681466.7905 | 37861227.7409 | 46344746.3923 | 55132022.7447 | 64223056.7983 | 65438087.6025 | 66653118.4068 | 67868149.2111 | 69083180.0154 | 70298210.8197 | 71513241.624 | 72728272.4283 | 73943303.2326 | 75158334.0369 | 76373364.8412 | 77588395.6455 | 78803426.4497 | 80018457.254 | 81233488.0583 | 82448518.8626 | 83663549.6669 | 84878580.4712 | 86093611.2755 | 87308642.0798 | 88523672.8841 | 89738703.6884 | 90953734.4927 | 92168765.297 | 93383796.1012 | 94598826.9055 | 95813857.7098 | 97028888.5141 | 98243919.3184 | 99458950.1227 | 100673980.927 | 101889011.7313 | 103104042.5356 | 104319073.3399 | 105534104.1442 | 106749134.9484 | 107964165.7527 | 109179196.557 | 110394227.3613 | 111609258.1656 | 112824288.9699 | 114039319.7742 | 115254350.5785 | 116469381.3828 | 117684412.1871 | 118899442.9914 | 120114473.7956 | 121329504.5999
Number of Vacuum Salt Refining Plants in Design/Permitting |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of Vacuum Salt Refining Plants in Construction |  | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of Vacuum Salt Refining Plants in Operation |  | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Metric Tons of Vacuum Refined Salt Produced |  | 0 | 0 | 0 | 86687.5 | 173375 | 260062.5 | 346750 | 433437.5 | 520125 | 606812.5 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500 | 693500
Vacuum Salt Refining Capital Cost |  | 0 | 0 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum Salt Refining Operating Cost |  | 0 | 0 | 0 | 3604613.0586 | 7209226.1172 | 10813839.1757 | 14418452.2343 | 18023065.2929 | 21627678.3515 | 25232291.41 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686 | 28836904.4686
Vacuum Salt Refining Energy Cost (paid to geothermal) |  | 0 | 0 | 0 | 725428.8586 | 1450857.7172 | 2176286.5757 | 2901715.4343 | 3627144.2929 | 4352573.1515 | 5078002.01 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686 | 5803430.8686
Price of Refined Salt (2017 USGS trendline per metric tonne) | 3.33 | 190 | 193.33 | 196.66 | 199.99 | 203.32 | 206.65 | 209.98 | 213.31 | 216.64 | 219.97 | 223.3 | 226.63 | 229.96 | 233.29 | 236.62 | 239.95 | 243.28 | 246.61 | 249.94 | 253.27 | 256.6 | 259.93 | 263.26 | 266.59 | 269.92 | 273.25 | 276.58 | 279.91 | 283.24 | 286.57 | 289.9 | 293.23 | 296.56 | 299.89 | 303.22 | 306.55 | 309.88 | 313.21 | 316.54 | 319.87 | 323.2 | 326.53 | 329.86 | 333.19 | 336.52 | 339.85 | 343.18 | 346.51 | 349.84 | 353.17 | 356.5 | 359.83 | 363.16 | 366.49 | 369.82 | 373.15 | 376.48 | 379.81
Annual Revenue from Vacuum Refined Salt |  | 0 | 0 | 0 | 17336633.125 | 35250605 | 53741915.625 | 72810565 | 92456553.125 | 112679880 | 133480545.625 | 154858550 | 157167905 | 159477260 | 161786615 | 164095970 | 166405325 | 168714680 | 171024035 | 173333390 | 175642745 | 177952100 | 180261455 | 182570810 | 184880165 | 187189520 | 189498875 | 191808230 | 194117585 | 196426940 | 198736295 | 201045650 | 203355005 | 205664360 | 207973715 | 210283070 | 212592425 | 214901780 | 217211135 | 219520490 | 221829845 | 224139200 | 226448555 | 228757910 | 231067265 | 233376620 | 235685975 | 237995330 | 240304685 | 242614040 | 244923395 | 247232750 | 249542105 | 251851460 | 254160815 | 256470170 | 258779525 | 261088880 | 263398235
Number of 20 MGD VTE Plants in Design/Permitting |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of 20 MGD VTE Plants in Construction |  | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of 20 MGD VTE Plants in Operation |  | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4
20 MGD VTE Distillation Plants Capital Cost |  | 0 | 25578205.2904 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 51156410.5807 | 25578205.2904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 MGD VTE Distillation Plants Operating Cost |  | 0 | 0 | 0 | 4307000 | 8614000 | 12921000 | 17228000 | 21535000 | 25842000 | 30149000 | 34456000 | 38763000 | 43070000 | 47377000 | 51684000 | 55991000 | 60298000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 64605000 | 60298000 | 55991000 | 51684000 | 47377000 | 43070000 | 38763000 | 34456000 | 30149000 | 25842000 | 21535000 | 17228000
20 MGD VTE Distillation Plants Energy Cost (paid to geothermal) |  | 0 | 0 | 0 | 4493880 | 8987760 | 13481640 | 17975520 | 22469400 | 26963280 | 31457160 | 35951040 | 40444920 | 44938800 | 49432680 | 53926560 | 58420440 | 62914320 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 67408200 | 62914320 | 58420440 | 53926560 | 49432680 | 44938800 | 40444920 | 35951040 | 31457160 | 26963280 | 22469400 | 17975520
20 MGD VTE Acre-feet of Distilled Water Produced |  | 0 | 0 | 0 | 21282.5778 | 42565.1557 | 63847.7335 | 85130.3113 | 106412.8892 | 127695.467 | 148978.0448 | 170260.6227 | 191543.2005 | 212825.7783 | 234108.3561 | 255390.934 | 276673.5118 | 297956.0896 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 297956.0896 | 276673.5118 | 255390.934 | 234108.3561 | 212825.7783 | 191543.2005 | 170260.6227 | 148978.0448 | 127695.467 | 106412.8892 | 85130.3113
20 MGD VTE Concentration factor |  | 5 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
20 MGD VTE Acre-feet of Saturated Brine Produced |  | 0 | 0 | 0 | 4256.5156 | 8513.0311 | 15961.9334 | 21282.5778 | 26603.2223 | 31923.8667 | 49659.3483 | 56753.5409 | 63847.7335 | 53206.4446 | 58527.089 | 63847.7335 | 55334.7024 | 59591.2179 | 63847.7335 | 63847.7335 | 63847.7335 | 63847.7335 | 63847.7335 | 63847.7335 | 63847.7335 | 63847.7335 | 63847.7335 | 63847.7335 | 63847.7335 | 63847.7335 | 63847.7335 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 53206.4446 | 49659.3483 | 46112.252 | 42565.1557 | 39018.0594 | 35470.9631 | 31923.8667 | 28376.7704 | 24829.6741 | 21282.5778 | 17735.4815 | 14188.3852
20 MGD VTE Metric Tons of Salt in Brine |  | 0 | 0 | 0 | 1368760.2022 | 2737520.4043 | 5132850.7581 | 6843801.0108 | 8554751.2635 | 10265701.5162 | 15968869.0252 | 18250136.0288 | 20531403.0324 | 17109502.527 | 18820452.7797 | 20531403.0324 | 17793882.6281 | 19162642.8303 | 20531403.0324 | 20531403.0324 | 20531403.0324 | 20531403.0324 | 20531403.0324 | 20531403.0324 | 20531403.0324 | 20531403.0324 | 20531403.0324 | 20531403.0324 | 20531403.0324 | 20531403.0324 | 20531403.0324 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 17109502.527 | 15968869.0252 | 14828235.5234 | 13687602.0216 | 12546968.5198 | 11406335.018 | 10265701.5162 | 9125068.0144 | 7984434.5126 | 6843801.0108 | 5703167.509 | 4562534.0072
Acre-feet of Seawater drawn from Salton Sea (AFY) |  | 0 | 0 | 0 | 25539.0934 | 51078.1868 | 79809.6669 | 106412.8892 | 133016.1114 | 159619.3337 | 198637.3931 | 227014.1635 | 255390.934 | 266032.2229 | 292635.4452 | 319238.6675 | 332008.2142 | 357547.3076 | 383086.401 | 383086.401 | 383086.401 | 383086.401 | 383086.401 | 383086.401 | 383086.401 | 383086.401 | 383086.401 | 383086.401 | 383086.401 | 383086.401 | 383086.401 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 372445.1121 | 347615.4379 | 322785.7638 | 297956.0896 | 273126.4155 | 248296.7414 | 223467.0672 | 198637.3931 | 173807.719 | 148978.0448 | 124148.3707 | 99318.6965
Acre-feet of Distilled Water Sold to Customers (AFY) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170260.6227 | 191543.2005 | 212825.7783 | 234108.3561 | 255390.934 | 276673.5118 | 297956.0896 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 319238.6675 | 297956.0896 | 276673.5118 | 255390.934 | 234108.3561 | 212825.7783 | 191543.2005 | 170260.6227 | 148978.0448 | 127695.467 | 106412.8892 | 85130.3113
Price of water sold per AF | 0 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
Annual Revenue from Water Sold to Customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102156373.5912 | 114925920.2901 | 127695466.989 | 140465013.688 | 153234560.3869 | 166004107.0858 | 178773653.7847 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 191543200.4836 | 178773653.7847 | 166004107.0858 | 153234560.3869 | 140465013.688 | 127695466.989 | 114925920.2901 | 102156373.5912 | 89386826.8923 | 76617280.1934 | 63847733.4945 | 51078186.7956
Number of Groundwater Wellfields in Design/Permitting |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of Groundwater Wellfields in Construction |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of Groundwater Wellfields in Operation |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Groundwater Wellfields Capital Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Groundwater Wellfields Operating Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Acre-feet of Groundwater Water Produced |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Blend Ratio (groundwater/distilled water) |  | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333 | 2.3333
Acre-feet of Blended Water Delivered to Salton Sea Habitat |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Unit Cost of Blended Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Cost of Blended Water |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purified salt production from Salinity Gradient Solar Ponds
Number of 1 MGD Salt Separation Plants in Design/Permitting |  | 0 | 0 | 0 | 1 | 2 | 2 | 3 | 3 | 5 | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 7 | 7 | 8 | 7 | 8 | 6 | 7 | 7 | 6 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of 1 MGD Salt Separation Plants in Construction |  | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 3 | 3 | 5 | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 7 | 7 | 8 | 7 | 8 | 6 | 7 | 7 | 6 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of 1 MGD Salt Separation Plants in Operation |  | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 5 | 8 | 11 | 16 | 22 | 28 | 34 | 40 | 47 | 53 | 59 | 66 | 73 | 80 | 87 | 94 | 101 | 109 | 116 | 123 | 130 | 138 | 145 | 153 | 159 | 166 | 173 | 179 | 186 | 193 | 200 | 207 | 214 | 221 | 228 | 235 | 242 | 249 | 257 | 264 | 271 | 279 | 285 | 292 | 298 | 304 | 310 | 315 | 320 | 325 | 330
1 MGD Salt Separation Plants Capital Cost |  | 0 | 0 | 0 | 0 | 2612359.9775 | 5224719.955 | 5224719.955 | 7837079.9325 | 7837079.9325 | 13061799.8875 | 15674159.865 | 15674159.865 | 15674159.865 | 15674159.865 | 18286519.8425 | 15674159.865 | 15674159.865 | 18286519.8425 | 18286519.8425 | 18286519.8425 | 18286519.8425 | 18286519.8425 | 18286519.8425 | 20898879.82 | 18286519.8425 | 18286519.8425 | 18286519.8425 | 20898879.82 | 18286519.8425 | 20898879.82 | 15674159.865 | 18286519.8425 | 18286519.8425 | 15674159.865 | 18286519.8425 | 18286519.8425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 MGD Salt Separation Plants Operating Cost |  | 0 | 0 | 0 | 0 | 0 | 299944.0376 | 899832.1128 | 1499720.1881 | 2399552.3009 | 3299384.4137 | 4799104.6018 | 6598768.8275 | 8398433.0532 | 10198097.2788 | 11997761.5045 | 14097369.7678 | 15897033.9935 | 17696698.2192 | 19796306.4825 | 21895914.7457 | 23995523.009 | 26095131.2723 | 28194739.5356 | 30294347.7989 | 32693900.0998 | 34793508.3631 | 36893116.6264 | 38992724.8897 | 41392277.1906 | 43491885.4539 | 45891437.7548 | 47691101.9805 | 49790710.2437 | 51890318.507 | 53689982.7327 | 55789590.996 | 57889199.2593 | 59988807.5226 | 62088415.7859 | 64188024.0492 | 66287632.3125 | 68387240.5757 | 70486848.839 | 72586457.1023 | 74686065.3656 | 77085617.6665 | 79185225.9298 | 81284834.1931 | 83684386.494 | 85484050.7197 | 87583658.983 | 89383323.2086 | 91182987.4343 | 92982651.66 | 94482371.8481 | 95982092.0361 | 97481812.2242 | 98981532.4123
1 MGD Salt Separation Plants Energy Cost (paid to SGSP) |  | 0 | 0 | 0 | 0 | 0 | 123193.6718 | 369581.0155 | 615968.3591 | 985549.3746 | 1355130.39 | 1971098.7491 | 2710260.78 | 3449422.8109 | 4188584.8419 | 4927746.8728 | 5790102.5755 | 6529264.6064 | 7268426.6373 | 8130782.3401 | 8993138.0428 | 9855493.7455 | 10717849.4483 | 11580205.151 | 12442560.8537 | 13428110.2283 | 14290465.931 | 15152821.6338 | 16015177.3365 | 17000726.711 | 17863082.4138 | 18848631.7883 | 19587793.8193 | 20450149.522 | 21312505.2247 | 22051667.2556 | 22914022.9584 | 23776378.6611 | 24638734.3638 | 25501090.0666 | 26363445.7693 | 27225801.472 | 28088157.1748 | 28950512.8775 | 29812868.5802 | 30675224.283 | 31660773.6575 | 32523129.3603 | 33385485.063 | 34371034.4376 | 35110196.4685 | 35972552.1712 | 36711714.2021 | 37450876.233 | 38190038.2639 | 38806006.623 | 39421974.9821 | 40037943.3412 | 40653911.7003
Pecentage of Purified Salt sent to Vacuum Refining at Solar Ponds |  | 0% | 0% | 0% | 0% | 0% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.38% | 91.15% | 86.08% | 80.59% | 77.96% | 75.87% | 73.04% | 66.04% | 60.26% | 55.41% | 51.28% | 47.73% | 47.39% | 44.53% | 41.99% | 39.73% | 37.43% | 35.62% | 33.76% | 34.65% | 33.19% | 31.85% | 30.78% | 29.62% | 28.55% | 29.27% | 28.28% | 27.35% | 26.49% | 25.67% | 24.91% | 24.19% | 24.89% | 24.12% | 23.48% | 22.87% | 22.22% | 21.75% | 22.41% | 21.95% | 21.52% | 21.1% | 20.77% | 20.44% | 20.13% | 20.87%
Metric Tons of Solar Salt Produced at Solar Ponds |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11409.9291 | 75774.5567 | 140139.1844 | 229679.1667 | 294043.7943 | 358408.422 | 447948.4042 | 624175.8865 | 800403.3688 | 976630.851 | 1152858.3333 | 1329085.8156 | 1443801.1525 | 1620028.6347 | 1796256.117 | 1972483.5993 | 2173886.4361 | 2350113.9184 | 2551516.7553 | 2615881.3829 | 2792108.8652 | 2968336.3475 | 3119388.4751 | 3295615.9574 | 3471843.4397 | 3561383.4219 | 3737610.9042 | 3913838.3865 | 4090065.8687 | 4266293.351 | 4442520.8333 | 4618748.3155 | 4708288.2978 | 4909691.1347 | 5085918.617 | 5262146.0992 | 5463548.9361 | 5614601.0638 | 5704141.046 | 5855193.1737 | 6006245.3013 | 6157297.429 | 6283174.2021 | 6409050.9751 | 6534927.7481 | 6574117.0212
Salt Evaporation Ponds Capital Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 71584.0047 | 403813.0106 | 403813.0106 | 561759.0146 | 403813.0106 | 403813.0106 | 561759.0146 | 1105622.0281 | 1105622.0281 | 1105622.0281 | 1105622.0281 | 1105622.0281 | 719705.0186 | 1105622.0281 | 1105622.0281 | 1105622.0281 | 1263568.0321 | 1105622.0281 | 1263568.0321 | 403813.0106 | 1105622.0281 | 1105622.0281 | 947676.0241 | 1105622.0281 | 1105622.0281 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Salt Evaporation Ponds Operating Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4433.7126 | 29444.7584 | 54455.8042 | 89249.5827 | 114260.6285 | 139271.6743 | 174065.4528 | 242544.5816 | 311023.7105 | 379502.8393 | 447981.9682 | 516461.097 | 561037.6082 | 629516.737 | 697995.8659 | 766474.9947 | 844736.8563 | 913215.9851 | 991477.8467 | 1016488.8925 | 1084968.0213 | 1153447.1502 | 1212143.5463 | 1280622.6752 | 1349101.804 | 1383895.5825 | 1452374.7114 | 1520853.8402 | 1589332.9691 | 1657812.0979 | 1726291.2268 | 1794770.3556 | 1829564.1341 | 1907825.9956 | 1976305.1245 | 2044784.2533 | 2123046.1149 | 2181742.511 | 2216536.2895 | 2275232.6857 | 2333929.0818 | 2392625.478 | 2441539.1415 | 2490452.8049 | 2539366.4684 | 2554594.7815
Playa covered with solar salt evaporation ponds (acres) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5928 | 17.2192 | 31.8455 | 52.1927 | 66.8191 | 81.4454 | 101.7927 | 141.8389 | 181.8852 | 221.9315 | 261.9778 | 302.024 | 328.0922 | 368.1384 | 408.1847 | 448.231 | 493.9982 | 534.0444 | 579.8116 | 594.4379 | 634.4842 | 674.5305 | 708.8559 | 748.9021 | 788.9484 | 809.2957 | 849.3419 | 889.3882 | 929.4345 | 969.4808 | 1009.527 | 1049.5733 | 1069.9205 | 1115.6877 | 1155.734 | 1195.7803 | 1241.5474 | 1275.8728 | 1296.2201 | 1330.5454 | 1364.8708 | 1399.1962 | 1427.8007 | 1456.4051 | 1485.0096 | 1493.9151
Price of Solar Salt (2017 USGS trendline price per metric tonne) | 2.1 | 90 | 92.1 | 94.2 | 96.3 | 98.4 | 100.5 | 102.6 | 104.7 | 106.8 | 108.9 | 111 | 113.1 | 115.2 | 117.3 | 119.4 | 121.5 | 123.6 | 125.7 | 127.8 | 129.9 | 132 | 134.1 | 136.2 | 138.3 | 140.4 | 142.5 | 144.6 | 146.7 | 148.8 | 150.9 | 153 | 155.1 | 157.2 | 159.3 | 161.4 | 163.5 | 165.6 | 167.7 | 169.8 | 171.9 | 174 | 176.1 | 178.2 | 180.3 | 182.4 | 184.5 | 186.6 | 188.7 | 190.8 | 192.9 | 195 | 197.1 | 199.2 | 201.3 | 203.4 | 205.5 | 207.6 | 209.7
Annual Revenue from Solar Salt |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1314423.829 | 8888355.5044 | 16732618.6159 | 27906018.7486 | 36343812.9772 | 45051938.6418 | 57247806.0618 | 81080447.6573 | 105653244.6783 | 130966197.1249 | 157019304.9969 | 183812568.2945 | 202709681.8049 | 230854080.4482 | 259738634.517 | 289363344.0114 | 323474301.6972 | 354632190.2873 | 390382063.5582 | 405723202.4941 | 438919513.6108 | 472855980.153 | 503469299.8867 | 538833209.0353 | 574937273.6094 | 597243999.859 | 634646331.5342 | 672788818.6348 | 711671461.161 | 751294259.1127 | 791657212.49 | 832760321.2928 | 858791785.5211 | 905838014.3504 | 949032413.9244 | 992966968.924 | 1042445137.0086 | 1083056545.1996 | 1112307503.9758 | 1154058574.5338 | 1196444064.0281 | 1239463972.4585 | 1277997632.6975 | 1317059975.3832 | 1356651000.5158 | 1378592339.3452
Number of Vacuum Salt Refining Plants in Design/Permitting |  | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of Vacuum Salt Refining Plants in Construction |  | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Number of Vacuum Salt Refining Plants in Operation |  | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 14 | 14 | 14 | 14 | 14 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20
Metric Tons of Vacuum Refined Salt Produced |  | 0 | 0 | 0 | 0 | 0 | 86687.5 | 173375 | 260062.5 | 346750 | 433437.5 | 520125 | 606812.5 | 693500 | 780187.5 | 866875 | 953562.5 | 1040250 | 1126937.5 | 1213625 | 1213625 | 1213625 | 1213625 | 1213625 | 1213625 | 1300312.5 | 1300312.5 | 1300312.5 | 1300312.5 | 1300312.5 | 1300312.5 | 1300312.5 | 1387000 | 1387000 | 1387000 | 1387000 | 1387000 | 1387000 | 1473687.5 | 1473687.5 | 1473687.5 | 1473687.5 | 1473687.5 | 1473687.5 | 1473687.5 | 1560375 | 1560375 | 1560375 | 1560375 | 1560375 | 1560375 | 1647062.5 | 1647062.5 | 1647062.5 | 1647062.5 | 1647062.5 | 1647062.5 | 1647062.5 | 1733750
Vacuum Salt Refining Capital Cost |  | 0 | 0 | 0 | 0 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 2185910 | 0 | 0 | 0 | 0 | 0 | 2185910 | 0 | 0 | 0 | 0 | 0 | 0 | 2185910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Vacuum Salt Refining Operating Cost |  | 0 | 0 | 0 | 0 | 0 | 3604613.0586 | 7209226.1172 | 10813839.1757 | 14418452.2343 | 18023065.2929 | 21627678.3515 | 25232291.41 | 28836904.4686 | 32441517.5272 | 36046130.5858 | 39650743.6443 | 43255356.7029 | 46859969.7615 | 50464582.8201 | 50464582.8201 | 50464582.8201 | 50464582.8201 | 50464582.8201 | 50464582.8201 | 54069195.8786 | 54069195.8786 | 54069195.8786 | 54069195.8786 | 54069195.8786 | 54069195.8786 | 54069195.8786 | 57673808.9372 | 57673808.9372 | 57673808.9372 | 57673808.9372 | 57673808.9372 | 57673808.9372 | 61278421.9958 | 61278421.9958 | 61278421.9958 | 61278421.9958 | 61278421.9958 | 61278421.9958 | 61278421.9958 | 64883035.0544 | 64883035.0544 | 64883035.0544 | 64883035.0544 | 64883035.0544 | 64883035.0544 | 68487648.1129 | 68487648.1129 | 68487648.1129 | 68487648.1129 | 68487648.1129 | 68487648.1129 | 68487648.1129 | 72092261.1715
Vacuum Salt Refining Energy Cost (paid to geothermal) |  | 0 | 0 | 0 | 0 | 0 | 725428.8586 | 1450857.7172 | 2176286.5757 | 2901715.4343 | 3627144.2929 | 4352573.1515 | 5078002.01 | 5803430.8686 | 6528859.7272 | 7254288.5858 | 7979717.4443 | 8705146.3029 | 9430575.1615 | 10156004.0201 | 10156004.0201 | 10156004.0201 | 10156004.0201 | 10156004.0201 | 10156004.0201 | 10881432.8786 | 10881432.8786 | 10881432.8786 | 10881432.8786 | 10881432.8786 | 10881432.8786 | 10881432.8786 | 11606861.7372 | 11606861.7372 | 11606861.7372 | 11606861.7372 | 11606861.7372 | 11606861.7372 | 12332290.5958 | 12332290.5958 | 12332290.5958 | 12332290.5958 | 12332290.5958 | 12332290.5958 | 12332290.5958 | 13057719.4544 | 13057719.4544 | 13057719.4544 | 13057719.4544 | 13057719.4544 | 13057719.4544 | 13783148.3129 | 13783148.3129 | 13783148.3129 | 13783148.3129 | 13783148.3129 | 13783148.3129 | 13783148.3129 | 14508577.1715
Price of Refined Salt (2017 USGS trendline per metric tonne) | 3.33 | 190 | 193.33 | 196.66 | 199.99 | 203.32 | 206.65 | 209.98 | 213.31 | 216.64 | 219.97 | 223.3 | 226.63 | 229.96 | 233.29 | 236.62 | 239.95 | 243.28 | 246.61 | 249.94 | 253.27 | 256.6 | 259.93 | 263.26 | 266.59 | 269.92 | 273.25 | 276.58 | 279.91 | 283.24 | 286.57 | 289.9 | 293.23 | 296.56 | 299.89 | 303.22 | 306.55 | 309.88 | 313.21 | 316.54 | 319.87 | 323.2 | 326.53 | 329.86 | 333.19 | 336.52 | 339.85 | 343.18 | 346.51 | 349.84 | 353.17 | 356.5 | 359.83 | 363.16 | 366.49 | 369.82 | 373.15 | 376.48 | 379.81
Annual Revenue from Vacuum Refined Salt |  | 0 | 0 | 0 | 0 | 0 | 17913971.875 | 36405282.5 | 55473931.875 | 75119920 | 95343246.875 | 116143912.5 | 137521916.875 | 159477260 | 182009941.875 | 205119962.5 | 228807321.875 | 253072020 | 277914056.875 | 303333432.5 | 307374803.75 | 311416175 | 315457546.25 | 319498917.5 | 323540288.75 | 350980350 | 355310390.625 | 359640431.25 | 363970471.875 | 368300512.5 | 372630553.125 | 376960593.75 | 406710010 | 411328720 | 415947430 | 420566140 | 425184850 | 429803560 | 461573661.875 | 466481041.25 | 471388420.625 | 476295800 | 481203179.375 | 486110558.75 | 491017938.125 | 525097395 | 530293443.75 | 535489492.5 | 540685541.25 | 545881590 | 551077638.75 | 587177781.25 | 592662499.375 | 598147217.5 | 603631935.625 | 609116653.75 | 614601371.875 | 620086090 | 658495587.5
Domestic salt consumption trendline, from USGS data 2004-2017 |  | 59536000 | 60027300 | 60518600 | 61009900 | 61501200 | 61992500 | 62483800 | 62975100 | 63466400 | 63957700 | 64449000 | 64940300 | 65431600 | 65922900 | 66414200 | 66905500 | 67396800 | 67888100 | 68379400 | 68870700 | 69362000 | 69853300 | 70344600 | 70835900 | 71327200 | 71818500 | 72309800 | 72801100 | 73292400 | 73783700 | 74275000 | 74766300 | 75257600 | 75748900 | 76240200 | 76731500 | 77222800 | 77714100 | 78205400 | 78696700 | 79188000 | 79679300 | 80170600 | 80661900 | 81153200 | 81644500 | 82135800 | 82627100 | 83118400 | 83609700 | 84101000 | 84592300 | 85083600 | 85574900 | 86066200 | 86557500 | 87048800 | 87540100
Solar Salt sold into market (metric tonnes per year) |  | 0 | 0 | 0 | 72323.2622 | 144646.5243 | 216969.7865 | 289293.0486 | 361616.3108 | 433939.573 | 506262.8351 | 578586.0973 | 578586.0973 | 589996.0264 | 654360.654 | 718725.2817 | 808265.2639 | 872629.8916 | 936994.5193 | 1026534.5015 | 1202761.9838 | 1378989.4661 | 1555216.9483 | 1731444.4306 | 1907671.9129 | 2022387.2497 | 2198614.732 | 2374842.2143 | 2551069.6965 | 2752472.5334 | 2928700.0157 | 3130102.8526 | 3194467.4802 | 3370694.9625 | 3546922.4448 | 3697974.5724 | 3874202.0547 | 4050429.537 | 4139969.5192 | 4316197.0015 | 4492424.4838 | 4668651.966 | 4844879.4483 | 5021106.9306 | 5197334.4128 | 5286874.3951 | 5488277.232 | 5664504.7142 | 5840732.1965 | 6042135.0334 | 6193187.161 | 6282727.1433 | 6433779.271 | 6584831.3986 | 6735883.5263 | 6861760.2993 | 6987637.0724 | 7113513.8454 | 7152703.1185
Portion of Annual Domestic Solar Salt Consumption (2017 basis) |  | 0% | 0% | 0% | 1.317% | 2.613% | 3.889% | 5.144% | 6.38% | 7.597% | 8.795% | 9.975% | 9.899% | 10.02% | 11.03% | 12.02% | 13.42% | 14.39% | 15.34% | 16.68% | 19.4% | 22.09% | 24.74% | 27.35% | 29.92% | 31.5% | 34.01% | 36.49% | 38.94% | 41.73% | 44.1% | 46.82% | 47.47% | 49.77% | 52.03% | 53.89% | 56.1% | 58.28% | 59.19% | 61.32% | 63.43% | 65.51% | 67.56% | 69.59% | 71.59% | 72.39% | 74.69% | 76.63% | 78.54% | 80.77% | 82.3% | 83.01% | 84.51% | 85.99% | 87.46% | 88.59% | 89.7% | 90.8% | 90.79%
Refined Salt sold into market (metric tonnes per year) |  | 0 | 0 | 0 | 86687.5 | 173375 | 346750 | 520125 | 693500 | 866875 | 1040250 | 1213625 | 1300312.5 | 1387000 | 1473687.5 | 1560375 | 1647062.5 | 1733750 | 1820437.5 | 1907125 | 1907125 | 1907125 | 1907125 | 1907125 | 1907125 | 1993812.5 | 1993812.5 | 1993812.5 | 1993812.5 | 1993812.5 | 1993812.5 | 1993812.5 | 2080500 | 2080500 | 2080500 | 2080500 | 2080500 | 2080500 | 2167187.5 | 2167187.5 | 2167187.5 | 2167187.5 | 2167187.5 | 2167187.5 | 2167187.5 | 2253875 | 2253875 | 2253875 | 2253875 | 2253875 | 2253875 | 2340562.5 | 2340562.5 | 2340562.5 | 2340562.5 | 2340562.5 | 2340562.5 | 2340562.5 | 2427250
Portion of Annual Domestic Refined Salt Consumption (2017 basis) |  | 0% | 0% | 0% | 1.579% | 3.132% | 6.215% | 9.249% | 12.24% | 15.18% | 18.07% | 20.92% | 22.25% | 23.55% | 24.84% | 26.11% | 27.35% | 28.58% | 29.79% | 30.99% | 30.77% | 30.55% | 30.34% | 30.12% | 29.91% | 31.06% | 30.85% | 30.64% | 30.43% | 30.23% | 30.02% | 29.83% | 30.92% | 30.72% | 30.52% | 30.32% | 30.13% | 29.94% | 30.99% | 30.79% | 30.6% | 30.41% | 30.22% | 30.04% | 29.85% | 30.86% | 30.67% | 30.49% | 30.31% | 30.13% | 29.95% | 30.92% | 30.74% | 30.57% | 30.39% | 30.22% | 30.05% | 29.88% | 30.81%
Total Salts to Sale (metric tonnes per year) |  | 0 | 0 | 0 | 159010.7622 | 318021.5243 | 563719.7865 | 809418.0486 | 1055116.3108 | 1300814.573 | 1546512.8351 | 1792211.0973 | 1878898.5973 | 1976996.0264 | 2128048.154 | 2279100.2817 | 2455327.7639 | 2606379.8916 | 2757432.0193 | 2933659.5015 | 3109886.9838 | 3286114.4661 | 3462341.9483 | 3638569.4306 | 3814796.9129 | 4016199.7497 | 4192427.232 | 4368654.7143 | 4544882.1965 | 4746285.0334 | 4922512.5157 | 5123915.3526 | 5274967.4802 | 5451194.9625 | 5627422.4448 | 5778474.5724 | 5954702.0547 | 6130929.537 | 6307157.0192 | 6483384.5015 | 6659611.9838 | 6835839.466 | 7012066.9483 | 7188294.4306 | 7364521.9128 | 7540749.3951 | 7742152.232 | 7918379.7142 | 8094607.1965 | 8296010.0334 | 8447062.161 | 8623289.6433 | 8774341.771 | 8925393.8986 | 9076446.0263 | 9202322.7993 | 9328199.5724 | 9454076.3454 | 9579953.1185
All salts removed from Salton Sea system (metric tonnes per year) |  | 0 | 0 | 0 | 1689987.3658 | 3379974.7315 | 6208902.6359 | 8379133.3261 | 10549364.0163 | 12745277.5935 | 18933408.427 | 21751004.529 | 24273056.3543 | 21103350.5997 | 23119450.3018 | 25135550.004 | 22754037.2906 | 24427946.9422 | 26101856.5937 | 26457864.2847 | 26813871.9757 | 27169879.6667 | 27525887.3577 | 27881895.0486 | 28237902.7396 | 28644768.6722 | 29000776.3631 | 29356784.0541 | 29712791.7451 | 30119657.6776 | 30475665.3686 | 27460630.7957 | 27765780.2452 | 28121787.9361 | 28477795.6271 | 28782945.0765 | 29138952.7675 | 29494960.4585 | 29850968.1494 | 30206975.8404 | 30562983.5314 | 30918991.2224 | 31274998.9134 | 31631006.6043 | 31987014.2953 | 32343021.9863 | 32749887.9188 | 33105895.6098 | 32321269.799 | 31587502.2297 | 30752018.1773 | 29967392.3665 | 29131908.3141 | 28296424.2617 | 27460940.2093 | 26574597.9154 | 25688255.6214 | 24801913.3274 | 23915571.0335
Power & Water production from Salinity Gradient Solar Ponds
Mixed Salts to SGSP (metric tonnes per year) |  | 0 | 0 | 0 | 1530976.6036 | 3061953.2072 | 5645182.8494 | 7569715.2774 | 9494247.7055 | 11444463.0205 | 17386895.5918 | 19958793.4317 | 22394157.757 | 19126354.5734 | 20991402.1478 | 22856449.7223 | 20298709.5267 | 21821567.0506 | 23344424.5745 | 23524204.7832 | 23703984.9919 | 23883765.2006 | 24063545.4093 | 24243325.618 | 24423105.8267 | 24628568.9224 | 24808349.1311 | 24988129.3398 | 25167909.5485 | 25373372.6442 | 25553152.8529 | 22336715.4432 | 22490812.7649 | 22670592.9736 | 22850373.1823 | 23004470.5041 | 23184250.7128 | 23364030.9215 | 23543811.1302 | 23723591.3389 | 23903371.5476 | 24083151.7564 | 24262931.9651 | 24442712.1738 | 24622492.3825 | 24802272.5912 | 25007735.6869 | 25187515.8956 | 24226662.6025 | 23291492.1963 | 22304956.0163 | 21344102.7232 | 20357566.5431 | 19371030.3631 | 18384494.183 | 17372275.116 | 16360056.049 | 15347836.982 | 14335617.915
SGSP filled per year (square miles) |  | 0 | 0 | 0 | 0.39323 | 0.78646 | 1.45 | 1.9443 | 2.4386 | 2.9395 | 4.4658 | 5.1264 | 5.7519 | 4.9126 | 5.3916 | 5.8707 | 5.2137 | 5.6049 | 5.996 | 6.0422 | 6.0884 | 6.1345 | 6.1807 | 6.2269 | 6.2731 | 6.3258 | 6.372 | 6.4182 | 6.4644 | 6.5171 | 6.5633 | 5.7372 | 5.7768 | 5.8229 | 5.8691 | 5.9087 | 5.9549 | 6.001 | 6.0472 | 6.0934 | 6.1396 | 6.1857 | 6.2319 | 6.2781 | 6.3243 | 6.3705 | 6.4232 | 6.4694 | 6.2226 | 5.9824 | 5.729 | 5.4822 | 5.2288 | 4.9754 | 4.722 | 4.4621 | 4.2021 | 3.9421 | 3.6821
Cumulative SGSP brine fill (square miles) |  | 0 | 0 | 0 | 0.39323 | 1.1797 | 2.6297 | 4.5739 | 7.0125 | 9.952 | 14.4178 | 19.5442 | 25.2962 | 30.2088 | 35.6004 | 41.4711 | 46.6848 | 52.2896 | 58.2856 | 64.3278 | 70.4162 | 76.5507 | 82.7314 | 88.9583 | 95.2314 | 101.5572 | 107.9292 | 114.3474 | 120.8118 | 127.3289 | 133.8922 | 139.6294 | 145.4061 | 151.2291 | 157.0982 | 163.0069 | 168.9617 | 174.9628 | 181.01 | 187.1034 | 193.2429 | 199.4287 | 205.6606 | 211.9387 | 218.263 | 224.6334 | 231.0566 | 237.526 | 243.7486 | 249.7311 | 255.4601 | 260.9423 | 266.1711 | 271.1466 | 275.8686 | 280.3307 | 284.5327 | 288.4748 | 292.1569
Square Miles of SGSP in Design/Permitting |  | 0 | 0 | 0.39323 | 0.78646 | 1.45 | 1.9443 | 2.4386 | 2.9395 | 4.4658 | 5.1264 | 5.7519 | 4.9126 | 5.3916 | 5.8707 | 5.2137 | 5.6049 | 5.996 | 6.0422 | 6.0884 | 6.1345 | 6.1807 | 6.2269 | 6.2731 | 6.3258 | 6.372 | 6.4182 | 6.4644 | 6.5171 | 6.5633 | 5.7372 | 5.7768 | 5.8229 | 5.8691 | 5.9087 | 5.9549 | 6.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Square Miles of SGSP in Construction |  | 0 | 0 | 0 | 0.39323 | 0.78646 | 1.45 | 1.9443 | 2.4386 | 2.9395 | 4.4658 | 5.1264 | 5.7519 | 4.9126 | 5.3916 | 5.8707 | 5.2137 | 5.6049 | 5.996 | 6.0422 | 6.0884 | 6.1345 | 6.1807 | 6.2269 | 6.2731 | 6.3258 | 6.372 | 6.4182 | 6.4644 | 6.5171 | 6.5633 | 5.7372 | 5.7768 | 5.8229 | 5.8691 | 5.9087 | 5.9549 | 6.001 | 6.0472 | 6.0934 | 6.1396 | 6.1857 | 6.2319 | 6.2781 | 6.3243 | 6.3705 | 6.4232 | 6.4694 | 6.2226 | 5.9824 | 5.729 | 5.4822 | 5.2288 | 4.9754 | 4.722 | 4.4621 | 4.2021 | 3.9421 | 3.6821
Square Miles of SGSP in Operation |  | 0 | 0 | 0 | 0 | 0.39323 | 1.1797 | 2.6297 | 4.5739 | 7.0125 | 9.952 | 14.4178 | 19.5442 | 25.2962 | 30.2088 | 35.6004 | 41.4711 | 46.6848 | 52.2896 | 58.2856 | 64.3278 | 70.4162 | 76.5507 | 82.7314 | 88.9583 | 95.2314 | 101.5572 | 107.9292 | 114.3474 | 120.8118 | 127.3289 | 133.8922 | 139.6294 | 145.4061 | 151.2291 | 157.0982 | 163.0069 | 168.9617 | 174.9628 | 181.01 | 187.1034 | 193.2429 | 199.4287 | 205.6606 | 211.9387 | 218.263 | 224.6334 | 231.0566 | 237.526 | 243.7486 | 249.7311 | 255.4601 | 260.9423 | 266.1711 | 271.1466 | 275.8686 | 280.3307 | 284.5327 | 288.4748
SGSP Capital Cost |  | 0 | 0 | 0 | 41667518.0881 | 83335036.1761 | 153640988.3299 | 206019639.6878 | 258398291.0458 | 311475935.5525 | 473206961.4025 | 543204503.8274 | 609486109.202 | 520548598.3721 | 571308292.1263 | 622067985.8805 | 552455762.1439 | 593902308.9258 | 635348855.7077 | 640241807.7494 | 645134759.791 | 650027711.8326 | 654920663.8742 | 659813615.9158 | 664706567.9575 | 670298513.1479 | 675191465.1895 | 680084417.2311 | 684977369.2727 | 690569314.4632 | 695462266.5048 | 607922741.9724 | 612116700.8653 | 617009652.9069 | 621902604.9485 | 626096563.8413 | 630989515.8829 | 635882467.9246 | 640775419.9662 | 645668372.0078 | 650561324.0494 | 655454276.091 | 660347228.1327 | 665240180.1743 | 670133132.2159 | 675026084.2575 | 680618029.4479 | 685510981.4896 | 659360110.2903 | 633908232.2398 | 607058367.8917 | 580907496.6923 | 554057632.3442 | 527207767.9961 | 500357903.648 | 472809046.1511 | 445260188.6542 | 417711331.1573 | 390162473.6604
SGSP Operating Cost |  | 0 | 0 | 0 | 0 | 972138.0234 | 2916414.0702 | 6500986.7437 | 11307597.1323 | 17336245.2361 | 24603239.1494 | 35643553.0732 | 48316968.167 | 62536788.5135 | 74681622.3968 | 88010722.3613 | 102524088.4068 | 115413343.0895 | 129269580.3503 | 144092800.1892 | 159030176.689 | 174081709.8494 | 189247399.6706 | 204527246.1525 | 219921249.2952 | 235429409.0987 | 251068033.6572 | 266820814.8765 | 282687752.7566 | 298668847.2973 | 314780406.5933 | 331006122.5499 | 345189468.2323 | 359470662.4809 | 373866013.3903 | 388375520.9605 | 402982877.097 | 417704389.8942 | 432540059.3522 | 447489885.4709 | 462553868.2504 | 477732007.6906 | 493024303.7916 | 508430756.5533 | 523951365.9757 | 539586132.0589 | 555335054.8029 | 571214442.3019 | 587207986.4617 | 602591408.9391 | 617381017.8285 | 631544196.941 | 645097254.3712 | 658023882.0245 | 670324079.901 | 681997848.0007 | 693028878.2292 | 703417170.5865 | 713162725.0726
MWh of Power Produced (baseload seasonal average) |  | 0 | 0 | 0 | 0 | 32298.1891 | 96894.5672 | 215987.9502 | 375682.1575 | 575977.1893 | 817414.8635 | 1184216.838 | 1605276.7564 | 2077714.2447 | 2481212.6487 | 2924056.9572 | 3406247.1702 | 3834478.1154 | 4294835.9659 | 4787320.7215 | 5283598.2035 | 5783668.4117 | 6287531.3461 | 6795187.0068 | 7306635.3938 | 7821876.5071 | 8341452.1646 | 8864820.5484 | 9391981.6585 | 9922935.4948 | 10458223.8754 | 10997304.9823 | 11468530.641 | 11943007.208 | 12421276.5012 | 12903338.5206 | 13388651.4483 | 13877757.1023 | 14370655.4825 | 14867346.589 | 15367830.4217 | 15872106.9807 | 16380176.266 | 16892038.2775 | 17407693.0153 | 17927140.4794 | 18450380.6697 | 18977955.4043 | 19509322.8652 | 20020419.7215 | 20511787.7913 | 20982343.4384 | 21432628.4811 | 21862101.1011 | 22270761.2985 | 22658609.0734 | 23025102.6075 | 23370241.9011 | 23694026.954
MW Power Capacity (baseload seasonal average) |  | 0 | 0 | 0 | 0 | 3.687 | 11.061 | 24.6562 | 42.8861 | 65.7508 | 93.3122 | 135.1846 | 183.2508 | 237.182 | 283.2435 | 333.7965 | 388.841 | 437.7258 | 490.2781 | 546.4978 | 603.1505 | 660.2361 | 717.7547 | 775.7063 | 834.0908 | 892.9083 | 952.2206 | 1011.9658 | 1072.144 | 1132.7552 | 1193.8612 | 1255.4001 | 1309.193 | 1363.357 | 1417.9539 | 1472.9838 | 1528.3849 | 1584.2188 | 1640.4858 | 1697.1857 | 1754.3185 | 1811.8844 | 1869.8831 | 1928.3149 | 1987.1796 | 2046.4772 | 2106.2078 | 2166.4333 | 2227.0917 | 2285.436 | 2341.5283 | 2395.2447 | 2446.6471 | 2495.6736 | 2542.3243 | 2586.5992 | 2628.4364 | 2667.8358 | 2704.7976
MW Power Capacity Increment (baseload seasonal average) |  | 0 | 0 | 0 | 0 | 3.687 | 7.374 | 13.5951 | 18.2299 | 22.8647 | 27.5614 | 41.8724 | 48.0662 | 53.9312 | 46.0615 | 50.553 | 55.0445 | 48.8848 | 52.5523 | 56.2197 | 56.6527 | 57.0856 | 57.5186 | 57.9516 | 58.3845 | 58.8175 | 59.3123 | 59.7452 | 60.1782 | 60.6112 | 61.106 | 61.5389 | 53.7929 | 54.164 | 54.597 | 55.0299 | 55.401 | 55.834 | 56.2669 | 56.6999 | 57.1329 | 57.5658 | 57.9988 | 58.4317 | 58.8647 | 59.2977 | 59.7306 | 60.2254 | 60.6584 | 58.3444 | 56.0922 | 53.7164 | 51.4024 | 49.0266 | 46.6507 | 44.2749 | 41.8372 | 39.3995 | 36.9618
Price per MWh (current local baseload renewable contract rate) |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
Annual Revenue from Power Sold |  | 0 | 0 | 0 | 0 | 2745346.0707 | 8236038.212 | 18358975.7653 | 31932983.3916 | 48958061.091 | 69480263.3966 | 100658431.2287 | 136448524.2935 | 176605710.7976 | 210903075.1405 | 248544841.3627 | 289531009.4641 | 325930639.8096 | 365061057.0982 | 406922261.3301 | 449105847.2943 | 491611814.9908 | 534440164.4195 | 577590895.5806 | 621064008.4739 | 664859503.0995 | 709023433.9906 | 753509746.614 | 798318440.9696 | 843449517.0576 | 888949029.411 | 934770923.4968 | 974825104.4877 | 1015155612.6778 | 1055808502.6001 | 1096783774.2548 | 1138035373.1085 | 1179609353.6946 | 1221505716.0129 | 1263724460.0635 | 1306265585.8464 | 1349129093.3616 | 1392314982.6091 | 1435823253.5888 | 1479653906.3009 | 1523806940.7452 | 1568282356.9219 | 1613126209.364 | 1658292443.5384 | 1701735676.325 | 1743501962.257 | 1783499192.268 | 1821773420.8913 | 1858278593.5935 | 1893014710.3748 | 1925981771.2351 | 1957133721.6413 | 1986470561.5933 | 2013992291.0911
Acre-feet of Distilled Water Produced by SGSP (25% water/power) |  | 0 | 0 | 0 | 0 | 450.2052 | 1350.6155 | 3010.6608 | 5236.6418 | 8028.5587 | 11393.9637 | 16506.8245 | 22375.9879 | 28961.3044 | 34585.6775 | 40758.4941 | 47479.754 | 53448.8746 | 59865.8127 | 66730.5686 | 73648.1913 | 80618.6809 | 87642.0374 | 94718.2608 | 101847.351 | 109029.3082 | 116271.6847 | 123566.9281 | 130915.0384 | 138316.0155 | 145777.412 | 153291.6754 | 159860.1002 | 166473.8395 | 173140.4456 | 179859.9187 | 186624.7062 | 193442.3607 | 200312.882 | 207236.2702 | 214212.5254 | 221241.6474 | 228323.6363 | 235458.4921 | 242646.2148 | 249886.8044 | 257180.2609 | 264534.1367 | 271940.8794 | 279065.0697 | 285914.26 | 292473.3455 | 298749.8786 | 304736.3068 | 310432.6303 | 315838.8489 | 320947.4103 | 325758.3145 | 330271.5615
Acre-feet of Distilled Water Consumed for SGSP Surface Make-up |  | 0 | 0 | 0 | 0 | 334.2459 | 1002.7378 | 2235.2056 | 3887.8413 | 5960.6448 | 8459.2233 | 12255.1657 | 16612.6102 | 21501.7483 | 25677.453 | 30260.3387 | 35250.4054 | 39682.061 | 44446.19 | 49542.7923 | 54678.6446 | 59853.7469 | 65068.0992 | 70321.7015 | 75614.5537 | 80946.6559 | 86323.6153 | 91739.8246 | 97195.2839 | 102689.9932 | 108229.5596 | 113808.376 | 118684.9733 | 123595.2133 | 128544.7034 | 133533.4434 | 138555.8263 | 143617.4591 | 148718.342 | 153858.4748 | 159037.8576 | 164256.4903 | 169514.3731 | 174811.5058 | 180147.8886 | 185523.5213 | 190938.404 | 196398.1438 | 201897.1335 | 207186.3479 | 212271.3939 | 217141.0574 | 221800.9454 | 226245.4508 | 230474.5736 | 234488.3138 | 238281.0643 | 241852.8251 | 245203.5961
Acre-feet of Distilled Water Available (solar) |  | 0 | 0 | 0 | 0 | 115.9592 | 347.8777 | 775.4552 | 1348.8006 | 2067.9139 | 2934.7404 | 4251.6587 | 5763.3777 | 7459.5561 | 8908.2245 | 10498.1554 | 12229.3486 | 13766.8136 | 15419.6228 | 17187.7762 | 18969.5466 | 20764.9339 | 22573.9381 | 24396.5593 | 26232.7973 | 28082.6523 | 29948.0694 | 31827.1035 | 33719.7544 | 35626.0223 | 37547.8524 | 39483.2994 | 41175.1269 | 42878.6261 | 44595.7423 | 46326.4753 | 48068.88 | 49824.9016 | 51594.5401 | 53377.7955 | 55174.6678 | 56985.157 | 58809.2632 | 60646.9863 | 62498.3262 | 64363.2831 | 66241.8569 | 68135.9929 | 70043.7458 | 71878.7218 | 73642.8661 | 75332.2881 | 76948.9332 | 78490.8561 | 79958.0567 | 81350.5351 | 82666.346 | 83905.4895 | 85067.9654
Price of water sold per AF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Revenue from Water Sold to Customers |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Acre-feet of Seawater drawn by SGSP (25% water/power) |  | 0 | 0 | 0 | 0 | 562.7565 | 1688.2694 | 3763.326 | 6545.8023 | 10035.6983 | 14242.4546 | 20633.5306 | 27969.9849 | 36201.6305 | 43232.0969 | 50948.1176 | 59349.6925 | 66811.0932 | 74832.2659 | 83413.2107 | 92060.2391 | 100773.3511 | 109552.5467 | 118397.8259 | 127309.1888 | 136286.6353 | 145339.6059 | 154458.6601 | 163643.798 | 172895.0194 | 182221.765 | 191614.5942 | 199825.1252 | 208092.2993 | 216425.557 | 224824.8984 | 233280.8828 | 241802.9509 | 250391.1025 | 259045.3378 | 267765.6567 | 276552.0592 | 285404.5454 | 294323.1151 | 303307.7685 | 312358.5055 | 321475.3261 | 330667.6709 | 339926.0992 | 348831.3371 | 357392.825 | 365591.6818 | 373437.3482 | 380920.3835 | 388040.7879 | 394798.5612 | 401184.2629 | 407197.8932 | 412839.4519
Acre-feet of distilled water supplied to habitat or Salton Sea |  | 0 | 0 | 0 | 21282.5778 | 42681.1149 | 64195.6112 | 85905.7665 | 107761.6897 | 129763.3809 | 151912.7853 | 4251.6587 | 5763.3777 | 7459.5561 | 8908.2245 | 10498.1554 | 12229.3486 | 13766.8136 | 15419.6228 | 17187.7762 | 18969.5466 | 20764.9339 | 22573.9381 | 24396.5593 | 26232.7973 | 28082.6523 | 29948.0694 | 31827.1035 | 33719.7544 | 35626.0223 | 37547.8524 | 39483.2994 | 41175.1269 | 42878.6261 | 44595.7423 | 46326.4753 | 48068.88 | 49824.9016 | 51594.5401 | 53377.7955 | 55174.6678 | 56985.157 | 58809.2632 | 60646.9863 | 62498.3262 | 64363.2831 | 66241.8569 | 68135.9929 | 70043.7458 | 71878.7218 | 73642.8661 | 75332.2881 | 76948.9332 | 78490.8561 | 79958.0567 | 81350.5351 | 82666.346 | 83905.4895 | 85067.9654
Acres of habitat sustained with distilled water by SGSP |  | 0 | 0 | 0 | 0 | 20.4634 | 61.3902 | 136.845 | 238.0236 | 364.926 | 517.8954 | 750.2927 | 1017.0667 | 1316.3923 | 1572.0396 | 1852.6157 | 2158.1203 | 2429.4377 | 2721.1099 | 3033.137 | 3347.5671 | 3664.4001 | 3983.6361 | 4305.2752 | 4629.3172 | 4955.7622 | 5284.9534 | 5616.5477 | 5950.5449 | 6286.9451 | 6626.0916 | 6967.6411 | 7266.1989 | 7566.8164 | 7869.8369 | 8175.2603 | 8482.7435 | 8792.6297 | 9104.9188 | 9419.611 | 9736.7061 | 10056.2042 | 10378.1053 | 10702.4093 | 11029.1164 | 11358.2264 | 11689.7395 | 12023.9988 | 12360.661 | 12684.4803 | 12995.7999 | 13293.9332 | 13579.2235 | 13851.3275 | 14110.2453 | 14355.9768 | 14588.1787 | 14806.8511 | 15011.9939
Acres of land covered (can be dust emmitting playa) |  | 0 | 0 | 0 | 16.4349 | 305.0007 | 865.6974 | 1885.5629 | 3247.5138 | 4951.5501 | 7002.237 | 10109.1907 | 13656.8639 | 17640.0158 | 21054.3495 | 24800.1952 | 28883.2738 | 32505.9935 | 36399.4009 | 40569.217 | 44790.688 | 49044.115 | 53329.4978 | 57646.8366 | 61996.1313 | 66363.4037 | 70781.1754 | 75230.9029 | 79712.5863 | 84231.9466 | 88782.107 | 93369.9442 | 97354.9192 | 101392.7049 | 105462.4466 | 109558.4232 | 113687.5115 | 117848.5558 | 122021.8569 | 126246.8129 | 130503.7249 | 134792.5928 | 139113.4166 | 143466.1963 | 147850.9319 | 152247.9244 | 156702.2927 | 161187.4612 | 165704.5856 | 170056.6393 | 174231.0248 | 178216.0755 | 182044.3127 | 185697.1932 | 189174.7171 | 192471.1633 | 195587.6878 | 198524.2904 | 201261.2721
Total Seawater drawn from Salton Sea (AFY) |  | 0 | 0 | 0 | 25539.0934 | 51640.9433 | 81497.9362 | 110176.2151 | 139561.9137 | 169655.0321 | 212879.8477 | 247647.6941 | 283360.9189 | 302233.8534 | 335867.5421 | 370186.7851 | 391357.9067 | 424358.4008 | 457918.6669 | 466499.6117 | 475146.64 | 483859.752 | 492638.9477 | 501484.2269 | 510395.5898 | 519373.0362 | 528426.0069 | 537545.0611 | 546730.1989 | 555981.4204 | 565308.166 | 564059.7063 | 572270.2373 | 580537.4114 | 588870.6691 | 597270.0104 | 605725.9949 | 614248.0629 | 622836.2146 | 631490.4499 | 640210.7688 | 648997.1713 | 657849.6574 | 666768.2272 | 675752.8806 | 684803.6176 | 693920.4382 | 703112.7829 | 687541.5372 | 671617.1009 | 655348.9146 | 638718.0973 | 621734.0896 | 604387.4508 | 586678.181 | 568606.2801 | 550162.3077 | 531346.2638 | 512158.1484
Total Metric tons of salt held by SGSP |  | 0 | 0 | 0 | 0 | 819248.1398 | 2457744.4193 | 5478564.9447 | 9529231.1307 | 14609742.9771 | 20733843.7754 | 30037827.8053 | 40718072.2667 | 52701516.064 | 62936310.2262 | 74169118.8272 | 86399941.867 | 97262080.4395 | 108939122.5126 | 121431068.0863 | 134019216.6987 | 146703568.35 | 159484123.04 | 172360880.7687 | 185333841.5363 | 198403005.3426 | 211582115.4789 | 224857428.654 | 238228944.8679 | 251696664.1205 | 265274329.7032 | 278948198.3246 | 290900903.8934 | 302936069.2097 | 315067437.5647 | 327295008.9585 | 339605040.0999 | 352011274.28 | 364513711.4989 | 377112351.7565 | 389807195.0529 | 402598241.3881 | 415485490.7621 | 428468943.1748 | 441548598.6263 | 454724457.1166 | 467996518.6456 | 481378526.5047 | 494856737.4026 | 507820781.5449 | 520284402.2231 | 532220112.8545 | 543641656.7305 | 554535290.5598 | 564901014.3424 | 574738828.0782 | 584034988.4761 | 592789495.536 | 601002349.2579
Annual Metric Tons of Salt Removed |  | 0 | 0 | 819248.1398 | 1638496.2795 | 3020820.5254 | 4050666.1859 | 5080511.8465 | 6124100.7983 | 9303984.0299 | 10680244.4613 | 11983443.7973 | 10234794.1621 | 11232808.601 | 12230823.0399 | 10862138.5725 | 11677042.0731 | 12491945.5737 | 12588148.6125 | 12684351.6512 | 12780554.69 | 12876757.7288 | 12972960.7675 | 13069163.8063 | 13179110.1363 | 13275313.1751 | 13371516.2139 | 13467719.2526 | 13577665.5827 | 13673868.6214 | 11952705.5688 | 12035165.3163 | 12131368.355 | 12227571.3938 | 12310031.1413 | 12406234.1801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Value of Salt Removal (per metric ton) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Revenue from Salt Removal |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Private Salton Sea Restoration Enterprise Overall Finanacials
Total Revenue |  | 0 | 0 | 0 | 24301363.271 | 52229169.0638 | 101697389.2533 | 157256290.0558 | 217724696.1324 | 283102607.4832 | 353436078.6413 | 538040324.1182 | 611502354.0612 | 691223240.0225 | 771921150.419 | 856811132.8809 | 948951992.9932 | 1034348048.1954 | 1123322560.527 | 1206323393.6081 | 1279905378.2221 | 1354549899.9938 | 1430256958.9234 | 1507026555.0108 | 1584858688.256 | 1678515743.4463 | 1758678499.41 | 1839903792.5315 | 1922191622.8108 | 2009288083.0139 | 2093799910.3867 | 2183226104.1726 | 2271895226.1538 | 2353565141.2648 | 2436297593.5336 | 2516029280.7263 | 2600787884.5329 | 2686609025.4973 | 2786106601.7446 | 2874159442.6496 | 2963274820.7125 | 3053452735.9332 | 3144693188.3117 | 3236996177.848 | 3330361704.5421 | 3438150045.894 | 3538392125.4543 | 3635150812.0247 | 3720202489.054 | 3809074777.7806 | 3887403359.7591 | 3983506530.1517 | 4059771386.5634 | 4134901605.9903 | 4208897188.4323 | 4276637466.762 | 4343091317.0843 | 4408258739.3993 | 4486886144.3319
Total Capital Costs |  | 0 | 25578205.2904 | 70296064.7457 | 111963582.8338 | 158429370.8994 | 231347683.0306 | 283726334.3885 | 338717345.724 | 391794990.2308 | 558750736.0358 | 612220984.2731 | 678574173.6525 | 589968891.8285 | 640728585.5827 | 694258585.3184 | 621876055.6003 | 637744397.0918 | 656383044.5649 | 659633949.62 | 664526901.6616 | 669419853.7032 | 674312805.7448 | 679205757.7865 | 688511062.7961 | 689690655.0185 | 694583607.0601 | 699476559.1017 | 707139817.1249 | 709961456.3338 | 717624714.3569 | 626186624.8481 | 631508842.7359 | 636401794.7775 | 638524440.8376 | 645488705.7119 | 650381657.7536 | 635882467.9246 | 640775419.9662 | 645668372.0078 | 650561324.0494 | 655454276.091 | 660347228.1327 | 665240180.1743 | 670133132.2159 | 675026084.2575 | 680618029.4479 | 685510981.4896 | 659360110.2903 | 633908232.2398 | 607058367.8917 | 580907496.6923 | 554057632.3442 | 527207767.9961 | 500357903.648 | 472809046.1511 | 445260188.6542 | 417711331.1573 | 390162473.6604
Capital Cost Inflation | 1.5% | 101.5% | 103% | 104.6% | 106.1% | 107.7% | 109.3% | 111% | 112.6% | 114.3% | 116.1% | 117.8% | 119.6% | 121.4% | 123.2% | 125% | 126.9% | 128.8% | 130.7% | 132.7% | 134.7% | 136.7% | 138.8% | 140.8% | 143% | 145.1% | 147.3% | 149.5% | 151.7% | 154% | 156.3% | 158.7% | 161% | 163.4% | 165.9% | 168.4% | 170.9% | 173.5% | 176.1% | 178.7% | 181.4% | 184.1% | 186.9% | 189.7% | 192.5% | 195.4% | 198.4% | 201.3% | 204.3% | 207.4% | 210.5% | 213.7% | 216.9% | 220.1% | 223.4% | 226.8% | 230.2% | 233.6% | 237.2%
Inflation Adjusted Total Capital Costs |  | 0 | 26351306.5453 | 73507074.7522 | 118834065.8172 | 170673427.0154 | 252965565.6385 | 314892228.8774 | 381562578.9093 | 447974464.2395 | 648453040.1824 | 721165057.8788 | 811315612.7034 | 715958190.5821 | 789221107.1109 | 867984345.9151 | 789151726.9889 | 821427749.3521 | 858116226.8308 | 875301761.1193 | 895021384.4901 | 915135653.6658 | 935651971.1053 | 956577872.5459 | 984228500.3113 | 1000703451.6708 | 1022919900.569 | 1045577684.6575 | 1072888214.9719 | 1093326807.5923 | 1121704996.7467 | 993461626.5505 | 1016934047.8506 | 1040185486.8334 | 1059309731.2502 | 1086926372.7367 | 1111593006.1201 | 1103114045.5257 | 1128276257.7507 | 1153945135.6822 | 1180130217.7937 | 1206841214.713 | 1234088012.2408 | 1261880674.4212 | 1290229446.6643 | 1319144758.9228 | 1350023700.1547 | 1380124933.7533 | 1347388070.2172 | 1314808375.6487 | 1278005027.8702 | 1241295371.0529 | 1201680845.7716 | 1160598593.2734 | 1118013495.0099 | 1072304431.8083 | 1024972543.6743 | 975979430.3991 | 925285904.9034
Total Operating Costs |  | 2371160 | 2371160 | 2371160 | 18202777.4931 | 35006533.0096 | 57535606.176 | 80790113.6786 | 106604658.8963 | 134064379.5386 | 162762445.9904 | 290580107.8717 | 318923271.1392 | 348817273.372 | 376656866.4749 | 405680725.6588 | 436321771.366 | 464905785.2682 | 494456781.7486 | 516606801.2493 | 534574620.8438 | 552656597.0992 | 570852730.0152 | 589163019.592 | 607587465.8296 | 630855345.7368 | 649524413.3902 | 668307637.7044 | 687205018.6793 | 706649476.7571 | 725791479.1479 | 745480558.6416 | 766557783.5434 | 783869420.887 | 801295214.8913 | 818402245.1142 | 836040044.3455 | 853792000.2377 | 875954469.3573 | 893934738.5709 | 912029164.4453 | 930237746.9804 | 948560486.1762 | 966997382.0328 | 985548434.5501 | 1008510000.2949 | 1027722286.5759 | 1046632117.1698 | 1056855224.4245 | 1066901130.4389 | 1075487381.981 | 1088176480.7552 | 1095526180.8381 | 1102249451.1442 | 1108346291.6734 | 1113383781.9837 | 1117778534.4228 | 1121530548.9908 | 1128936182.2543
Annual Net Revenue |  | -2371160 | -2371160 | -2371160 | 6098585.778 | 17222636.0542 | 44161783.0773 | 76466176.3772 | 111120037.2361 | 149038227.9446 | 190673632.6509 | 247460216.2466 | 292579082.922 | 342405966.6505 | 395264283.9441 | 451130407.222 | 512630221.6272 | 569442262.9271 | 628865778.7783 | 689716592.3588 | 745330757.3782 | 801893302.8947 | 859404228.9082 | 917863535.4188 | 977271222.4264 | 1047660397.7094 | 1109154086.0197 | 1171596154.8271 | 1234986604.1315 | 1302638606.2568 | 1368008431.2388 | 1437745545.5311 | 1505337442.6103 | 1569695720.3778 | 1635002378.6424 | 1697627035.6121 | 1764747840.1874 | 1832817025.2597 | 1910152132.3873 | 1980224704.0787 | 2051245656.2672 | 2123214988.9528 | 2196132702.1355 | 2269998795.8152 | 2344813269.992 | 2429640045.5991 | 2510669838.8784 | 2588518694.8549 | 2663347264.6296 | 2742173647.3418 | 2811915977.7781 | 2895330049.3964 | 2964245205.7253 | 3032652154.8461 | 3100550896.7589 | 3163253684.7783 | 3225312782.6615 | 3286728190.4085 | 3357949962.0776
Cumulative Net Revenue |  | -2371160 | -4742320 | -7113480 | -1014894.222 | 16207741.8322 | 60369524.9095 | 136835701.2867 | 247955738.5228 | 396993966.4674 | 587667599.1184 | 835127815.3649 | 1127706898.2869 | 1470112864.9375 | 1865377148.8816 | 2316507556.1036 | 2829137777.7308 | 3398580040.6579 | 4027445819.4362 | 4717162411.7951 | 5462493169.1733 | 6264386472.068 | 7123790700.9761 | 8041654236.3949 | 9018925458.8213 | 10066585856.5308 | 11175739942.5505 | 12347336097.3776 | 13582322701.509 | 14884961307.7658 | 16252969739.0046 | 17690715284.5357 | 19196052727.146 | 20765748447.5238 | 22400750826.1662 | 24098377861.7783 | 25863125701.9657 | 27695942727.2254 | 29606094859.6126 | 31586319563.6913 | 33637565219.9585 | 35760780208.9114 | 37956912911.0468 | 40226911706.8621 | 42571724976.8541 | 45001365022.4532 | 47512034861.3316 | 50100553556.1865 | 52763900820.816 | 55506074468.1578 | 58317990445.9359 | 61213320495.3324 | 64177565701.0576 | 67210217855.9037 | 70310768752.6627 | 73474022437.4409 | 76699335220.1024 | 79986063410.5109 | 83344013372.5885
Capital Repayment |  | 0 | 0 | 0 | 6098585.778 | 17222636.0542 | 44161783.0773 | 76466176.3772 | 111120037.2361 | 149038227.9446 | 190673632.6509 | 247460216.2466 | 292579082.922 | 342405966.6505 | 395264283.9441 | 451130407.222 | 512630221.6272 | 569442262.9271 | 628865778.7783 | 689716592.3588 | 745330757.3782 | 801893302.8947 | 859404228.9082 | 917863535.4188 | 977271222.4264 | 1047660397.7094 | 1109154086.0197 | 1171596154.8271 | 1234986604.1315 | 1302638606.2568 | 1368008431.2388 | 1437745545.5311 | 1505337442.6103 | 1569695720.3778 | 1635002378.6424 | 1697627035.6121 | 1764747840.1874 | 1832817025.2597 | 1910152132.3873 | 1980224704.0787 | 2051245656.2672 | 2123214988.9528 | 2196132702.1355 | 2269998795.8152 | 2344813269.992 | 2429640045.5991 | 2510669838.8784 | 2588518694.8549 | 2663347264.6296 | 2742173647.3418 | 2811915977.7781 | 2895330049.3964 | 2964245205.7253 | 3032652154.8461 | 3100550896.7589 | 3163253684.7783 | 3225312782.6615 | 3286728190.4085 | 3357949962.0776
Cumulative Capital Outlay |  | 2371160 | 30320525.2904 | 102987750.0361 | 208852747.0919 | 350059481.9371 | 537245381.8904 | 744505539.9017 | 972102848.3896 | 1214859610.6757 | 1582936714.0605 | 1947697482.0871 | 2333692572.8176 | 2581255497.9955 | 2826719799.6341 | 3069847977.7304 | 3179093811.7035 | 3247395945.8682 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548 | 3274913211.6548
Operating Cost Inflation | 1.5% | 101.5% | 103% | 104.6% | 106.1% | 107.7% | 109.3% | 111% | 112.6% | 114.3% | 116.1% | 117.8% | 119.6% | 121.4% | 123.2% | 125% | 126.9% | 128.8% | 130.7% | 132.7% | 134.7% | 136.7% | 138.8% | 140.8% | 143% | 145.1% | 147.3% | 149.5% | 151.7% | 154% | 156.3% | 158.7% | 161% | 163.4% | 165.9% | 168.4% | 170.9% | 173.5% | 176.1% | 178.7% | 181.4% | 184.1% | 186.9% | 189.7% | 192.5% | 195.4% | 198.4% | 201.3% | 204.3% | 207.4% | 210.5% | 213.7% | 216.9% | 220.1% | 223.4% | 226.8% | 230.2% | 233.6% | 237.2%
Inflation Adjusted Total Operating Costs |  | 2406727.4 | 2442828.311 | 2479470.7357 | 19319764.5513 | 37711978.0426 | 62911921.01 | 89664496.6789 | 120089357.9432 | 153287867.6219 | 188892463.3528 | 342288529.2972 | 381310458.276 | 423308054.6217 | 463949253.7856 | 507195052.0423 | 553686021.9904 | 598808103.3641 | 646423443.4427 | 685511779.9807 | 719994504.4581 | 755513529.2765 | 792094525.7144 | 829763737.1344 | 868547990.8962 | 915336633.011 | 956560796.4381 | 998986375.4223 | 1042642696.6146 | 1088226423.5855 | 1134470305.2569 | 1182724604.7127 | 1234406641.6443 | 1281218252.1645 | 1329345854.992 | 1378092251.4212 | 1428909095.2239 | 1481138409.8915 | 1542379123.5604 | 1597649331.9372 | 1654437693.5467 | 1712780423.423 | 1772714528.0607 | 1834277821.7085 | 1897508942.9852 | 1970843367.7399 | 2038514091.641 | 2107162569.7874 | 2159660706.0584 | 2212892136.3487 | 2264161659.3744 | 2325238417.7191 | 2376057562.7925 | 2426499077.0083 | 2476519511.7347 | 2525092050.2546 | 2573084989.1493 | 2620447818.2255 | 2677317290.8591
Cumulative Private Capital Invested |  | 2406727.4 | 31200862.2563 | 107187407.7441 | 226021473.5613 | 396694900.5767 | 649660466.2152 | 964552695.0926 | 1346115274.0019 | 1794089738.2414 | 2442542778.4238 | 3163707836.3026 | 3975023449.0061 | 4690981639.5882 | 5480202746.6991 | 6348187092.6142 | 7137338819.6031 | 7958766568.9552 | 8816882795.7861 | 9692184556.9053 | 10587205941.3954 | 11502341595.0613 | 12437993566.1666 | 13394571438.7126 | 14378799939.0239 | 15379503390.6947 | 16402423291.2637 | 17448000975.9212 | 18520889190.8931 | 19614215998.4854 | 20735920995.2321 | 21729382621.7827 | 22746316669.6333 | 23786502156.4667 | 24845811887.717 | 25932738260.4537 | 27044331266.5738 | 28147445312.0995 | 29275721569.8502 | 30429666705.5324 | 31609796923.3261 | 32816638138.0391 | 34050726150.2799 | 35312606824.7011 | 36602836271.3654 | 37921981030.2882 | 39272004730.4429 | 40652129664.1962 | 41999517734.4134 | 43314326110.0621 | 44592331137.9323 | 45833626508.9852 | 47035307354.7568 | 48195905948.0302 | 49313919443.04 | 50386223874.8483 | 51411196418.5226 | 52387175848.9218 | 53312461753.8251
Private Funds Borrowed | 10% | 2647400.14 | 31673548.3419 | 83585200.0366 | 125237713.8072 | 171771859.5936 | 235598107.1348 | 272030479.0506 | 312319964.7921 | 349975696.816 | 532300367.3832 | 577954589.3635 | 639236088.61 | 492847305.6994 | 529374131.5253 | 570205091.5842 | 433274331.5847 | 424476584.9729 | 419338820.7212 | 389939162.241 | 368621561.7988 | 347709211.2434 | 327238491.686 | 307246560.1365 | 294709583.2467 | 261276775.3591 | 242882417.3568 | 225126294.3032 | 212673217.6532 | 189491662.9803 | 178612930.7786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cumulative Private Debt |  | 2647400.14 | 34087840.2696 | 114671546.3555 | 229812229.9609 | 381348720.7958 | 583368406.1369 | 804032276.7942 | 1045555793.4703 | 1303468474.1347 | 1720996162.7793 | 2147414030.2193 | 2597566557.9301 | 2861693585.4092 | 3139090592.0219 | 3432893267.1313 | 3563895342.8764 | 3674564710.1353 | 3770351681.8096 | 3828304784.6292 | 3859837414.9512 | 3867681191.4715 | 3854363590.1941 | 3822226695.4504 | 3780382533.6022 | 3708790015.4969 | 3625106985.8143 | 3531036270.1919 | 3432795568.9471 | 3320023578.5838 | 3206302626.9933 | 2923982073.2944 | 2666520338.0894 | 2431728558.9351 | 2217610606.5547 | 2022346114.3448 | 1844275002.1653 | 1681883362.8357 | 1533790591.3502 | 1398737647.3883 | 1275576351.3317 | 1163259622.7855 | 1060832578.6145 | 967424414.814 | 882241003.1944 | 804558139.9423 | 733715388.6564 | 669110465.5156 | 610194118.8428 | 556465459.5312 | 507467702.6362 | 462784283.9263 | 422035318.3791 | 384874370.5128 | 350985509.0957 | 320080621.1933 | 291896962.7193 | 266194924.6633 | 242755996.0076
Interest Rate on Plant Construction Loans | bar: 90 to 209.7
Term of Plant Construction Loans |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
Annual Loan Repayment (monthly installments) |  | 233108.2123 | 3001493.9508 | 10097030.2017 | 20235368.7587 | 33578421.7937 | 51366608.3932 | 70796448.1161 | 92063016.1515 | 114772678.7386 | 151536721.9236 | 189083560.8992 | 228720278.2204 | 251977124.9125 | 276402416.4748 | 302272255.8396 | 313807217.714 | 323551849.047 | 331986059.4214 | 337088931.4769 | 339865434.723 | 340556092.9634 | 339383454.8802 | 336553745.0949 | 332869293.4644 | 326565447.0395 | 319197009.9256 | 310913918.898 | 302263653.3436 | 292333882.3691 | 282320553.6989 | 257461735.205 | 234791779.1543 | 214117952.3805 | 195264492.2099 | 178071112.1795 | 162391639.3296 | 148092771.4855 | 135052943.9619 | 123161296.0566 | 112316728.5463 | 102427044.1709 | 93408163.8005 | 85183411.6196 | 77682863.2521 | 70842751.2859 | 64604923.1407 | 58916346.6729 | 53728659.3116 | 48997756.895 | 44683418.7099 | 40748965.5472 | 37160947.8663 | 33888861.4172 | 30904887.9023 | 28183658.474 | 25702038.056 | 23438928.6557 | 21375089.9961
Annual Profit/Loss |  | -2639835.6123 | -5444322.2618 | -12576500.9374 | -15253770.039 | -19061230.7726 | -12581140.15 | -3204654.7392 | 5572322.0377 | 15042061.1227 | 13006893.3649 | 6668233.9219 | 1471617.5649 | 15938060.4883 | 31569480.1585 | 47343824.999 | 81458753.2889 | 111988095.7843 | 144913057.6628 | 183722682.1506 | 220045439.0409 | 258480277.7539 | 298778978.3288 | 340709072.7815 | 383441403.8954 | 436613663.3958 | 482920693.0463 | 530003498.2112 | 577285272.8527 | 628727777.0593 | 677009051.4309 | 743039764.2549 | 802696805.3552 | 858228936.7198 | 911687246.3317 | 959865917.1256 | 1009487149.9794 | 1057377844.1204 | 1108674534.2223 | 1153348814.6558 | 1196520398.6196 | 1238245268.3393 | 1278570496.4505 | 1317534944.5199 | 1355169898.3047 | 1396463926.8683 | 1435273110.6725 | 1469071895.5645 | 1506813123.684 | 1547184884.5369 | 1578558281.6748 | 1617519146.8854 | 1646552875.9046 | 1674513667.5648 | 1701472788.7953 | 1723361758.0334 | 1744304289.8791 | 1764371992.518 | 1788193763.4767
Annual Pretax Return on Investment |  | -0.0724% | -0.0724% | -0.0724% | 0.1862% | 0.5259% | 1.348% | 2.335% | 3.393% | 4.551% | 5.822% | 7.556% | 8.934% | 10.46% | 12.07% | 13.78% | 15.65% | 17.39% | 19.2% | 21.06% | 22.76% | 24.49% | 26.24% | 28.03% | 29.84% | 31.99% | 33.87% | 35.77% | 37.71% | 39.78% | 41.77% | 43.9% | 45.97% | 47.93% | 49.93% | 51.84% | 53.89% | 55.97% | 58.33% | 60.47% | 62.64% | 64.83% | 67.06% | 69.31% | 71.6% | 74.19% | 76.66% | 79.04% | 81.33% | 83.73% | 85.86% | 88.41% | 90.51% | 92.6% | 94.68% | 96.59% | 98.49% | 100.4% | 102.5%
Annual Geothermal Steam and Power Payment to CalEnergy |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Operating Cash |  | 7564.5277 | 2292211.4626 | 28587970.6659 | 95724394.1048 | 191614063.0079 | 317821700.3484 | 485935393.1777 | 669565536.5987 | 870536071.0179 | 1085550015.9619 | 1432917206.2624 | 1787722562.7916 | 2161673455.3154 | 2381438965.0696 | 2612252746.2151 | 2856202369.1764 | 2965125056.5676 | 3057148512.6416 | 3136725705.6605 | 3184861469.5019 | 3211025815.5596 | 3217490597.4176 | 3206357895.686 | 3179595437.1863 | 3144700227.2219 | 3085107778.2915 | 3015462083.7455 | 2937192626.8278 | 2855424548.0508 | 2761606681.6775 | 2673560210.9988 | 2452283095.594 | 2249772008.8216 | 2069988121.6362 | 1895285658.7337 | 1742169146.0246 | 1636147161.4304 | 1514188867.8218 | 1398141326.3619 | 1291966532.1576 | 1194663676.4117 | 1105315062.8242 | 1023078684.9127 | 947181454.8349 | 881877307.8877 | 818964799.1742 | 758057427.3268 | 769619172.3096 | 788841968.4194 | 808020956.4408 | 839008059.7588 | 866907348.5121 | 898789444.8042 | 934444802.8811 | 971137947.4184 | 1011228708.924 | 1054587486.7822 | 1105663854.581
Geothermal Steam & Power Purchase Agreement (Privately Funded) |  | 0 | 0 | 0 | 5997415.8586 | 11994831.7172 | 18717676.4343 | 25440521.1515 | 32163365.8686 | 38886210.5858 | 45609055.3029 | 52331900.0201 | 57551208.8786 | 62770517.7372 | 67989826.5958 | 73209135.4544 | 78428444.3129 | 83647753.1715 | 88867062.0301 | 89592490.8887 | 89592490.8887 | 89592490.8887 | 89592490.8887 | 89592490.8887 | 89592490.8887 | 90317919.7472 | 90317919.7472 | 90317919.7472 | 90317919.7472 | 90317919.7472 | 90317919.7472 | 90317919.7472 | 91043348.6058 | 91043348.6058 | 91043348.6058 | 91043348.6058 | 91043348.6058 | 91043348.6058 | 91768777.4644 | 91768777.4644 | 91768777.4644 | 91768777.4644 | 91768777.4644 | 91768777.4644 | 91768777.4644 | 92494206.323 | 92494206.323 | 92494206.323 | 88000326.323 | 83506446.323 | 79012566.323 | 75244115.1815 | 70750235.1815 | 66256355.1815 | 61762475.1815 | 57268595.1815 | 52774715.1815 | 48280835.1815 | 44512384.0401

## Management Team Cost
Category | Annual Salary | Benefits | Annual Cost
CEO | 180000 | 54000 | 234000
CFO | 160000 | 48000 | 208000
CTO | 150000 | 45000 | 195000
VP Business Development | 150000 | 45000 | 195000
Office Manager | 80000 | 24000 | 104000
Management Team Subtotal |  |  | 936000
Outside Consulting Services | 50000 |  | 50000
CPA Services | 10000 |  | 10000
Office Rent | 12000 |  | 12000
Office Supplies | 5000 |  | 5000
Travel Expenses | 10000 |  | 10000
Promotional Materials | 5000 |  | 5000
Electrical Service | 2160 |  | 2160
Water/Sewer/Trash Service | 1800 |  | 1800
Phone and Internet Service | 1200 |  | 1200
Operating Expense Subtotal |  |  | 97160

## Engineering Team Cost
Category | Annual Salary | Benefits | Annual Cost
Civil Engineer | 200000 | 60000 | 260000
Mechanical Engineer | 200000 | 60000 | 260000
Chemical Engineer | 180000 | 54000 | 234000
Electrical Engineer | 180000 | 54000 | 234000
CAD Designer | 75000 | 22500 | 97500
Permitting Specialist | 100000 | 30000 | 130000
Budgeting Specialist | 75000 | 22500 | 97500
Engineering Team Subtotal |  |  | 1313000
Computer Systems | 9000 |  | 9000
Engineering/CAD Software | 6000 |  | 6000
Office Supplies & Services | 5000 |  | 5000
Travel Expenses | 5000 |  | 5000
Engineering Team Expenses |  |  | 25000

## Energy Cost Rates
Steam Press | [10 empty] | VTE Plant Steam Requirement
20 | psig | 22 | lb/hr | 1 | kWh | 0.12 | $/kWh | 5.4545 | 1,000 lb/hr |  | 120000 | lb/hr | 5160436.3636 | $/year/5MGD
20 | psig | 30 | lb/hr | 1 | kWh | 0.12 | $/kWh | 4 | 1,000 lb/hr |  | 120000 | lb/hr | 3784320 | $/year/5MGD
20 | psig | 1156.2 | Btu/lb | 959.9 | Btu/lb | 3.9674 | Btu/kcal | 115188000 | Btu/hr |  | 33758.2668 | kWht
Steam Press |  | hg |  | hfg |  | Btu/kcal |  | Salt Plant Thermal Requirement |  |  | Salt Plant Steam Requirement
20 | psig | 1156.2 | Btu/lb | 959.9 | Btu/lb | 3.9674 | Btu/kcal | 1250000 | kcal/hr |  | 5166.388 | lb/hr | 222.1735 | $/year/250 tonne/day
20 | psig | 22 | lb/hr | 1 | kWh | 0.12 | $/kWh | 0.0054545 | $/lb/hr
Thermal Energy Cost | [10 empty] | Conversion
20 | psig | 22 | lb/hr | 1 | kWh | 0.12 | $/kWh | 5.4545 | $/1,000 lb/hr |  | 3412.142 | Btu/hr/kWt
20 | psig | 1156.2 | Btu/lb | 959.9 | Btu/lb |  |  | 5.6824e-06 | $/Btu/hr |  | 0.019389 | $/kWht
Black Rock Steam | Press. (psig) | Press. (psia) | Temp. (°F) | Hfg (Btu/lb) | Hf (Btu/lb) | Hg (Btu/lb)
HP Steam Flash | 255 | 269.71 | 402.72 | 823.8 | 377.99 | 1201.8
SP Steam Flash | 135 | 149.71 | 355.6 | 866.3 | 327.63 | 1193.9
VTE Steam Delivery 251°F | 15.661 | 30.371 | 251 | 944.7 | 219.65 | 1164.4
VTE Steam Delivery 233°F | 7.28 | 21.99 | 233 | 956.6 | 201.41 | 1158
VTE Steam Delivery 212°F | 0 | 14.71 | 212 | 970.1 | 180.21 | 1150.3
Quoted Steam Cost | [8 empty] | 0.00029307 | kWt/Btu/hr
255 | psig | 1201.8 | Btu/lb |  | 0.0045 | $/lb/hr | 3.7444e-06 | $/Btu/hr | 0.012776 | $/kWht
Quoted Power Cost |  |  |  |  | 0.085 | $/kWhe

## 45MGD 40 Effect Levellized VTE
Description | Cost | Unit
Plant capital cost | 218422709.836 | each
Amortizaton period | 30 | years
Interest rate | 6% | per year
Plant life capital cost | 471439621.3949
Annualized capital cost | 15714654.0465 |  | 0.26411
Distillate capacity | 45331000 | gpd | 171596.5356 | m3/day
Concentration factor | 6.174
Brine Capacity | 7342241.6586 | gpd
Recovery ratio | 86.06%
Plant availability | 95%
Plant spec cost | 4.8184
Plant Operating Costs
Operation & maintenance | 8438365.65 | per year
Chemicals | 992748.9 | per year
Maintenance Supplies | 330916.3 | per year
Annual O&M Cost | 15927597.5037
Plant Energy Costs
Electrical requirement | 11.6886 | MW
Electrical requirement | 209188.4017 | kWh/day
Electrical rate | 0.085 | per kWh
Electrical cost | 6165566.6537 | per year
Thermal requirement | 365680 | lbs/hr
Thermal rate | 0.0045 | per lb/hr
Thermal cost | 13694350.32 | per year
Annual Energy Cost | 19859916.9737
Annualized Plant Cost | 51502168.524
Distillate cost | 3.2765 | per 1,000 gal
Distillate cost | 1067.6674 | per acre-ft
Annual Distillate Output | 48238.0268 | AFY
Enthalpy of Evaporation | 937 | Btu/lb
Thermal Use per m3 | 14.0448 | kWht/m3
Electrical Use per MG | 4614.6876 | kWh/MG

## Levellized Salt Refinery Plant
Description | per cubic meter | Cost | Unit
Salt Refinery total capital cost |  | 2185910
Vacuum Crystallizing Plant | 25369589.3258 | 1400000 | each plant
Amortizaton period |  | 30 | years
Interest rate |  | 6% | per year
Plant life capital cost |  | 3021734.6468
Annualized capital cost |  | 100724.4882
Dewatering Centrifuge |  | 2790 | each unit
Pusher Centrifuge |  | 83120 | each unit
Amortizaton period |  | 15 | years
Interest rate |  | 6% | per year
Unit life capital cost |  | 130492.3322
Annualized capital cost |  | 8699.4888
Drying, Sorting, Packing Plant |  | 700000 | each plant
Amortizaton period |  | 15 | years
Interest rate |  | 6% | per year
Plant life capital cost |  | 1063259.6033
Annualized capital cost |  | 70883.9736
Salt Capacity |  | 250 | tonne/day
Input salt concentration | 310000
Crystallizing Plant Capacity | 5830564.7841
Crystallizing Plant Slurry Density |  | 15% | by weight
Brine Slurry Capacity | 264.172 | 374243.6667 | gpd
Water Recovery ratio |  | 75%
Plant availability |  | 95%
Plant spec cost |  | 2800 | $/tonne/day
Plant Operating Costs
Vacuum Crystallizing Plant parts | 0.0079 | 168000 | per year
Dewatering Centrifuge parts | 0.0228 | 10309.2 | per year
Drying, Sorting, Packing parts | 0.0475 | 84000 | per year
Replacements & Supplies | 0.0782 | 262309.2 | per year
Manpower |  | 1750000 | per year
Operating Supplies |  | 866875 | per year
Annual O&M Cost |  | 3604613.0586
Plant Energy Costs
Evaporator Thermal Requirement | 2250.5511 | 54013.2269 | kWht/day
Drying Thermal Requirement | 1250000 | 34890 | kWht/day
Thermal Rate |  | 0.012776 | $/kWht
Thermal Cost |  | 393859.5302 | per year
VTE electrical requirement | 1529.6485 | 1529.6485 | kWhe/day
Centrifuge electrical requirement | 85 | 2040 | kWhe/day
Dry/Sort electrical requirement | 320 | 7680 | kWhe/day
Electrical rate |  | 0.085 | per kWhe
Electrical cost |  | 331569.3283 | per year
Annual Energy Cost |  | 725428.8586
Annualized Plant Cost |  | 4510349.8677
Salt cost (refinery only) |  | 52.03 | per tonne
Salt Price (2015 Domestic) |  | 182 | per tonne
Net |  | 129.97 | per tonne
Refinery Annual Ouput |  | 86687.5 | Metric tons
Refinery Annual net |  | 11266775.1323
Total Salt Supply to All Plants |  | 15747 | tonne/day
Number of Salt Refineries |  | 62.988
Electrical Use per Tonne |  | 44.9986 | kWhe/tonne
Thermal Use per Tonne |  | 355.6129 | kWht/tonne

## Levellized Salt Sep Plant
Description | per cubic meter | Cost | Unit
Salt Separation Plant |  | Cost to Feed 5 MGD VTE |  | Capacity Factor to 30 MGD | Cost to Feed 30 MGD VTE |  | Capacity Factor to 1 MGD | Cost to Feed 1 MGD Pond VTE
Plant capital cost |  | 16500000 | each | 6.3533 | 104828781.1773 | each | 0.15832 | 2612359.9775 | each
Amortizaton period |  | 30 | years |  | 30 | years |  | 30 | years
Interest rate |  | 6% | per year |  | 6% | per year |  | 6% | per year
Plant life capital cost |  | 35613301.1941 |  |  | 226260542.9016 |  |  | 5638470.467
Annualized capital cost |  | 1187110.0398 |  |  | 7542018.0967 |  |  | 187949.0156
Permeate capacity |  | 6316128 | gpd | 6.3533 | 40128000 | gpd | 0.15832 | 1000000 | gpd
Feed Capacity |  | 8421504 | gpd |  | 53504000 | gpd |  | 1333333.3333 | gpd
Reject capacity |  | 2105376 | gpd |  | 13376000 | gpd |  | 333333.3333 | gpd
Recovery ratio |  | 75% |  |  | 75% |  |  | 75%
Plant availability |  | 95% |  |  | 95% |  |  | 95%
Plant spec cost |  | 2.6124 | $/gpd |  | 2.6124 | $/gpd |  | 2.6124 | $/gpd
Plant Operating Costs
Chemicals | 0.0079 | 65743.8 | per year | 8.5639 | 563026.5704 | per year | 8.5639 | 4821731.0063 | per year
UF Membranes 20% rep | 0.0228 | 189741.6 | per year | 8.5639 | 1624937.4436 | per year | 8.5639 | 13915881.8916 | per year
NF Membranes 25% rep | 0.0475 | 395295 | per year | 8.5639 | 3385286.3408 | per year | 8.5639 | 28991420.6075 | per year
Cartridge Filters | 0.0005 | 4161 | per year | 8.5639 | 35634.5931 | per year | 8.5639 | 305172.8485 | per year
Cleaning Chemicals | 0.0004 | 3328.8 | per year | 8.5639 | 28507.6744 | per year | 8.5639 | 244138.2788 | per year
Replacements & Supplies | 0.0791 | 658270.2 | per year | 6.3533 | 4182161.3789 | per year | 0.15832 | 104220.5288 | per year
Manpower |  | 412000 | per year | 6.3533 | 2617542.8997 | per year | 0.15832 | 65229.837 | per year
Maintenance Supplies |  | 46107.7344 | per year | 6.3533 | 292934.4 | per year | 0.15832 | 7300 | per year
Annual O&M Cost |  | 1894484.9344 |  |  | 12036154.3413 |  |  | 299944.0376
Plant Energy Costs
Electrical requirement | 1.1 | 26400 | kWh/day | 6.3533 | 167726.0499 | kWh/day | 0.15832 | 4179.776 | kWh/day
Electrical rate |  | 0.085 | per kWh |  | 0.085 | per kWh |  | 0.085 | per kWh
Electrical cost |  | 778107 | per year |  | 4943515.6628 | per year |  | 123193.6718 | per year
Annualized Plant Cost |  | 3081594.9742 |  |  | 19578172.4381 |  |  | 487893.0532
Permeate cost |  | 1.407 | per 1,000 gal |  | 1.407 | per 1,000 gal |  | 1.407 | per 1,000 gal
Permeate cost |  | 458.4906 | per acre-ft |  | 458.4906 | per acre-ft |  | 458.4906 | per acre-ft
NaCl in Permeate |  | 19180 | mg/liter |  | 19180 | mg/liter |  | 19180 | mg/liter
Annual Permeate Output |  | 6721.1743 | AFY |  | 42701.3642 | AFY |  | 1064.1289 | AFY
Annual NaCl output |  | 159010.7622 | Metric Tons |  | 1010236.6298 | Metric Tons |  | 25175.3546 | Metric Tons
NaCl Cost in Brine |  | 19.3798 | per metric ton |  | 19.3798 | per metric ton |  | 19.3798 | per metric ton
Mixed Salts in Reject |  | 58700 | mg/liter |  | 58700 | mg/liter |  | 58700 | mg/liter
Annual Reject Output |  | 2240.3914 | AFY |  | 14233.7881 | AFY |  | 354.7096 | AFY
Annual Mixed Salt output |  | 162216.4014 | Metric Tons |  | 1030602.8879 | Metric Tons |  | 25682.887 | Metric Tons
Electrical Use per MG |  | 4179.776 | kWh/MG |  | 4179.776 | kWh/MG |  | 4179.776 | kWh/MG

## 45MGD 40 Effect VTE Capital Cos
Description | Cost 5 MGD | 40 Effect Scale Factor | Capacity Factor to 45.331 MGD | Cost 45 MGD
Evaporators 40 effect | 13597544.9133 |  |  | 118009768.4585
Deaerator | 35360 | 1 | 3.2545 | 115080.2987
Foundation | 180148.1481 | 2.6667 | 3.2545 | 1563461.7416
Excavation | 60000 | 2.6667 | 3.2545 | 520725.3333
Chemical feed system | 20000 | 1 | 3.2545 | 65090.6667
Pumps and Motors | 707000 | 2.6667 | 3.2545 | 6135880.1778
Steam ejector system | 50000 | 1 | 3.2545 | 162726.6667
Piping and valves | 300000 | 2.6667 | 3.2545 | 2603626.6667
Electrical gear & cables | 250000 | 2.6667 | 3.2545 | 2169688.8889
Instrumentation | 100000 | 2.6667 | 1 | 266666.6667
Computer control sytem | 50000 | 1 | 1 | 50000
Misc. bolts, nuts, gaskets | 10000 | 2.6667 | 3.2545 | 86787.5556
Subtotal Construction Equipment & Materials | 15360053.0615 |  |  | 131749503.121
Freight in (1.5% of materials) | 230400.7959 |  |  | 1976242.5468
Insurance (0.5% of materials) | 76800.2653 |  |  | 658747.5156
Mobilization | 167000 |  |  | 167000
Installation & site fabrication | 734000 | 2.6667 | 3.2545 | 6370206.5778
Subtotal Construction Contract | 1208201.0612 |  |  | 9172196.6402
Contractor markup (15% of above) | 2485238.1184 |  |  | 21138254.9642
Total Construction Contract | 19053492.2411 |  |  | 162059954.7253
Materials inspection (1.5% of materials) | 230400.7959 |  |  | 1976242.5468
Construction management (5% of contract) | 952674.6121 |  |  | 8102997.7363
Design & engineering (8% of contract) | 1524279.3793 |  |  | 12964796.378
Total Plant Costs | 21760847.0284 |  |  | 185103991.3864
Interest during construction (8% of total) | 1740867.7623 |  |  | 14808319.3109
Contingencies (10% of total) | 2176084.7028 |  |  | 18510399.1386
Total Plant Construction Project | 25677799.4935 |  |  | 218422709.836
8.5063

## 45MGD 40 Effect VTE Excavation
Description | Amount 1 | Unit | Amount 2 | Unit | Total Amount | Unit | Unit Cost | Unit | Cost 5 MGD | 40 Effect Scale Factor | Capacity Factor to 45.331 MGD | Cost 45 MGD
Demister Screens 316 SS | 1800 | ft² | 4 | inch | 600 | ft³ | 106 | ft³ | 63600 | 1.6667 | 3.5196 | 373077.6
Foundation | 4 | each | 320 | ft³ | 47.4074 | yd³ | 400 | yd³ | 18962.963 | 2.6667 | 3.2545 | 164574.9202
Excavation | 4 | each | 900 | ft³ | 133.3333 | yd³ | 50 | yd³ | 6666.6667 | 2.6667 | 3.2545 | 57858.3704

## 45MGD 40 Effect Pump Specs kW
Pump | Quantity | Flow Rate | Head | SG | Eff | HP | Total HP | Capacity Factor to 45.331 MGD | 45 MGD Total HP
|  | (gpm) | (ft)
Brine Recycle | 40 | 4342 | 45 | 1.2 | 75% | 78.9455 | 3157.8182 | 3.2545 | 10277.2245
Feed (DA) | 1 | 4342 | 90 | 1.03 | 82% | 123.954 | 123.954 | 3.2545 | 403.4124
Distillate | 1 | 3472 | 35 | 1 | 78% | 39.3421 | 39.3421 | 3.2545 | 128.0403
Brine Blowdown | 1 | 870 | 35 | 1.2 | 65% | 14.1958 | 14.1958 | 3.2545 | 46.2007
Condensate | 1 | 260 | 35 | 1 | 72% | 3.1916 | 3.1916 | 3.2545 | 10.3873
Seawater In | 1 | 8500 | 50 | 1.03 | 84% | 131.5987 | 131.5987 | 3.2545 | 428.2924
Coolant | 1 | 10000 | 35 | 1.03 | 75% | 121.3805 | 121.3805 | 3.2545 | 395.0368
Total HP | [6 empty] | 3591.481 |  | 11688.5945
Total KW | [6 empty] | 2678.1669 |  | 8716.1834
Material for all |  | Ni Resist
Impeller |  | 316L SS
Seals |  | Mechanical
Frequency |  | 60 Hz
Pump base |  | common

## 45MGD 40 Effect Evaporator Cost
Evaporator Components | Volume of Compnent 5 MGD 15 Effect | Material | Material | Weight 5 MGD | Unit Cost | Unit | Cost 5 MGD | 40 Effect Scale Factor | Capacity Factor to 45.331 MGD | Cost 45 MGD
| (ft³) |  |  | (tons)
Lower and Upper Deck | 698 | A285 grade C | A516 grade 70 | 171.01 | 1600 | ton | 273616 | 2.6667 | 3.2545 | 2374646.3801
Sidewalls | 140 | A285 grade C | A516 grade 70 | 34.3 | 1600 | ton | 54880 | 2.6667 | 3.2545 | 476290.1049
Endwalls | 24 | A285 grade C | A516 grade 70 | 5.88 | 1600 | ton | 9408 | 2.6667 | 3.2545 | 81649.7323
Endwall Chamfer | 8 | A285 grade C | A516 grade 70 | 1.96 | 1600 | ton | 3136 | 2.6667 | 3.2545 | 27216.5774
Lower and Upper Deck Lining | 116.3 | 316L SS | 316L SS | 29.075 | 4420 | ton | 128511.5 | 2.6667 | 3.2545 | 1115319.8946
Sidewalls Lining | 6.6667 | 316L SS | 316L SS | 1.6667 | 4420 | ton | 7366.6667 | 2.6667 | 3.2545 | 63933.4993
Endwall lining | 2 | 316L SS | 316L SS | 0.5 | 4420 | ton | 2210 | 2.6667 | 3.2545 | 19180.0498
Endwall Chamfer Lining | 1 | 316L SS | 316L SS | 0.25 | 4420 | ton | 1105 | 2.6667 | 3.2545 | 9590.0249
Effect Cylinder | 1433 | 316L SS | 316L SS | 358.25 | 4420 | ton | 1583465 | 2.6667 | 3.2545 | 13742505.6658
Effect Cylinder Cover | 147 | 316L SS | 316L SS | 36.75 | 4420 | ton | 162435 | 2.6667 | 3.2545 | 1409733.6587
Effect Bottom Cone | 183.3333 | 316L SS | 316L SS | 45.8333 | 4420 | ton | 202583.3333 | 2.6667 | 3.2545 | 1758171.2296
Tubesheet | 2160 | 316L SS | 316L SS | 540 | 4420 | ton | 2386800 | 2.6667 | 3.2545 | 20714453.76
Tubes | 1320 | 3" | Aluminum | 331.32 | 3454 | ton | 1144379.28 | 2.6667 | 3.2545 | 9931788.034
Demister | 360 | Mesh | 316L SS | 3 | 21600 | ton | 64800 | 2.6667 | 3.2545 | 562383.36
(ft)
Beams, Lower and Upper Deck | 1860 | Carbon Steel | W10x45# WF | 41.85 | 1540 | ton | 64449 | 2.6667 | 3.2545 | 559337.1168
Lower and Upper Deck Lining | 192 | Carbon Steel | W10x45# WF | 4.32 | 1540 | ton | 6652.8 | 2.6667 | 3.2545 | 57738.025
Lower and Upper Deck Lining | 640 | Carbon Steel | W10x45# WF | 14.4 | 1540 | ton | 22176 | 2.6667 | 3.2545 | 192460.0832
Tube Bundle Shop Fabrication | 15 | 316L SS | 90/10 CuNi |  | 477528.75 | each | 7162931.25 | 2.6667 | 3.2545 | 62165329.38
Nozzles, Manholes | 25 | 316L SS | 316L SS | 25 | 2666.67 | each | 66666.75 | 2.6667 | 3.2545 | 578584.4269
Paint |  | Blast Sand | Epoxy |  |  |  | 70000 | 2.6667 | 3.2545 | 607512.8889
Insulation / Lagging | 6664 | Fiberglass | Aluminum | 6664 | 10 | each | 66640 | 2.6667 | 3.2545 | 578352.2702
Platform, Stairs, Railing | 1133.3333 |  |  | 1133.3333 | 100 | each | 113333.3333 | 2.6667 | 3.2545 | 983592.2963
Evaporator Total |  |  |  | 1620.365 |  |  | 13597544.9133 |  |  | 118009768.4585
Deaerator | 31 | 316L SS | 316L SS | 8 | 4420 | ton | 35360 | 1 | 3.2545 | 115080.2987

## 30MGD 25 Effect Levellized VTE
Description | Cost | Unit
Plant capital cost | 147939759.1066 | each
Amortizaton period | 30 | years
Interest rate | 6% | per year
Plant life capital cost | 319310496.948
Annualized capital cost | 10643683.2316
Distillate capacity | 31368000 | gpd
Concentration factor | 6.203
Brine Capacity | 5056907.9478 | gpd
Recovery ratio | 92%
Plant availability | 90%
Plant spec cost | 4.7163
Plant Operating Costs
Operation & maintenance | 5839153.2 | per year
Chemicals | 686959.2 | per year
Maintenance Supplies | 228986.4 | per year
Annual O&M Cost | 10989119.5145
Plant Energy Costs
Electrical requirement | 8.4727 | MW
Electrical requirement | 151634.7288 | kWh/day
Electrical rate | 0.085 | per kWh
Electrical cost | 4234020.7145 | per year
Thermal requirement | 365680 | lbs/hr
Thermal rate | 0.0045 | per lb/hr
Thermal cost | 12973595.04 | per year
Annual Energy Cost | 17207615.7545
Annualized Plant Cost | 38840418.5007
Distillate cost | 3.7693 | per 1,000 gal
Distillate cost | 1228.242 | per acre-ft
Annual Distillate Output | 31622.7743 | AFY
Annual Brine Output | 5097.9807 | AFY
Electrical Use per MG | 4834.0579 | kWh/MG

## 30 MGD 25 Effect VTE Capital Co
Description | Cost 5 MGD | 25 Effect Scale Factor | Capacity Factor to 30.168 MGD | Cost 30 MGD
Evaporators 25 effect | 13597544.9133 |  |  | 79763198.4616
Deaerator | 35360 | 1 | 3.5196 | 124453.056
Foundation | 180148.1481 | 1.6667 | 3.5196 | 1056749.037
Excavation | 60000 | 1.6667 | 3.5196 | 351960
Chemical feed system | 20000 | 1 | 3.5196 | 70392
Pumps and Motors | 707000 | 1.6667 | 3.5196 | 4147262
Steam ejector system | 50000 | 1 | 3.5196 | 175980
Piping and valves | 300000 | 1.6667 | 3.5196 | 1759800
Electrical gear & cables | 250000 | 1.6667 | 3.5196 | 1466500
Instrumentation | 100000 | 1.6667 | 1 | 166666.6667
Computer control sytem | 50000 | 1 | 1 | 50000
Misc. bolts, nuts, gaskets | 10000 | 1.6667 | 3.5196 | 58660
Subtotal Construction Equipment & Materials | 15360053.0615 |  |  | 89191621.2213
Freight in (1.5% of materials) | 230400.7959 |  |  | 1337874.3183
Insurance (0.5% of materials) | 76800.2653 |  |  | 445958.1061
Mobilization | 167000 |  |  | 167000
Installation & site fabrication | 734000 | 1.6667 | 3.5196 | 4305644
Subtotal Construction Contract | 1208201.0612 |  |  | 6256476.4244
Contractor markup (15% of above) | 2485238.1184 |  |  | 14317214.6469
Total Construction Contract | 19053492.2411 |  |  | 109765312.2926
Materials inspection (1.5% of materials) | 230400.7959 |  |  | 1337874.3183
Construction management (5% of contract) | 952674.6121 |  |  | 5488265.6146
Design & engineering (8% of contract) | 1524279.3793 |  |  | 8781224.9834
Total Plant Costs | 21760847.0284 |  |  | 125372677.209
Interest during construction (8% of total) | 1740867.7623 |  |  | 10029814.1767
Contingencies (10% of total) | 2176084.7028 |  |  | 12537267.7209
Total Plant Construction Project | 25677799.4935 |  |  | 147939759.1066
5.7614

## 30MGD 25 Effect VTE Excavation
Description | Amount 1 | Unit | Amount 2 | Unit | Total Amount | Unit | Unit Cost | Unit | Cost 5 MGD | 25 Effect Scale Factor | Capacity Factor to 30.168 MGD | Cost 30 MGD
Demister Screens 316 SS | 1800 | ft² | 4 | inch | 600 | ft³ | 106 | ft³ | 63600 | 1.6667 | 3.5196 | 373077.6
Foundation | 4 | each | 320 | ft³ | 47.4074 | yd³ | 400 | yd³ | 18962.963 | 1.6667 | 3.5196 | 111236.7407
Excavation | 4 | each | 900 | ft³ | 133.3333 | yd³ | 50 | yd³ | 6666.6667 | 1.6667 | 3.5196 | 39106.6667

## 30MGD 25 Effect Pump Specs kW
Pump | Quantity | Flow Rate | Head | SG | Eff | HP | Total HP | Capacity Factor to 30.168 MGD | 30 MGD Total HP
|  | (gpm) | (ft)
Brine Recycle | 25 | 4342 | 45 | 1.2 | 75% | 78.9455 | 1973.6364 | 3.5196 | 6946.4105
Feed (DA) | 1 | 4342 | 90 | 1.03 | 82% | 123.954 | 123.954 | 3.5196 | 436.2685
Distillate | 1 | 3472 | 35 | 1 | 78% | 39.3421 | 39.3421 | 3.5196 | 138.4686
Brine Blowdown | 1 | 870 | 35 | 1.2 | 65% | 14.1958 | 14.1958 | 3.5196 | 49.9636
Condensate | 1 | 260 | 35 | 1 | 72% | 3.1916 | 3.1916 | 3.5196 | 11.2333
Seawater In | 1 | 8500 | 50 | 1.03 | 84% | 131.5987 | 131.5987 | 3.5196 | 463.1749
Coolant | 1 | 10000 | 35 | 1.03 | 75% | 121.3805 | 121.3805 | 3.5196 | 427.2107
Total HP | [6 empty] | 2407.2991 |  | 8472.73
Total KW | [6 empty] | 1795.1227 |  | 6318.1137
Material for all |  | Ni Resist
Impeller |  | 316L SS
Seals |  | Mechanical
Frequency |  | 60 Hz
Pump base |  | common

## 30MGD 25 Effect Evaporator Cost
Evaporator Components | Volume of Compnent 5 MGD 15 Effect | Material | Material | Weight 5 MGD | Unit Cost | Unit | Cost 5 MGD | 25 Effect Scale Factor | Capacity Factor 30.168 MGD | Cost 30 MGD
| (ft³) |  |  | (tons)
Lower and Upper Deck | 698 | A285 grade C | A516 grade 70 | 171.01 | 1600 | ton | 273616 | 1.6667 | 3.5196 | 1605031.456
Sidewalls | 140 | A285 grade C | A516 grade 70 | 34.3 | 1600 | ton | 54880 | 1.6667 | 3.5196 | 321926.08
Endwalls | 24 | A285 grade C | A516 grade 70 | 5.88 | 1600 | ton | 9408 | 1.6667 | 3.5196 | 55187.328
Endwall Chamfer | 8 | A285 grade C | A516 grade 70 | 1.96 | 1600 | ton | 3136 | 1.6667 | 3.5196 | 18395.776
Lower and Upper Deck Lining | 116.3 | 316L SS | 316L SS | 29.075 | 4420 | ton | 128511.5 | 1.6667 | 3.5196 | 753848.459
Sidewalls Lining | 6.6667 | 316L SS | 316L SS | 1.6667 | 4420 | ton | 7366.6667 | 1.6667 | 3.5196 | 43212.8667
Endwall lining | 2 | 316L SS | 316L SS | 0.5 | 4420 | ton | 2210 | 1.6667 | 3.5196 | 12963.86
Endwall Chamfer Lining | 1 | 316L SS | 316L SS | 0.25 | 4420 | ton | 1105 | 1.6667 | 3.5196 | 6481.93
Effect Cylinder | 1433 | 316L SS | 316L SS | 358.25 | 4420 | ton | 1583465 | 1.6667 | 3.5196 | 9288605.69
Effect Cylinder Cover | 147 | 316L SS | 316L SS | 36.75 | 4420 | ton | 162435 | 1.6667 | 3.5196 | 952843.71
Effect Bottom Cone | 183.3333 | 316L SS | 316L SS | 45.8333 | 4420 | ton | 202583.3333 | 1.6667 | 3.5196 | 1188353.8333
Tubesheet | 2160 | 316L SS | 316L SS | 540 | 4420 | ton | 2386800 | 1.6667 | 3.5196 | 14000968.8
Tubes | 1320 | 3" | Aluminum | 331.32 | 3454 | ton | 1144379.28 | 1.6667 | 3.5196 | 6712928.8565
Demister | 360 | Mesh | 316L SS | 3 | 21600 | ton | 64800 | 1.6667 | 3.5196 | 380116.8
(ft)
Beams, Lower and Upper Deck | 1860 | Carbon Steel | W10x45# WF | 41.85 | 1540 | ton | 64449 | 1.6667 | 3.5196 | 378057.834
Lower and Upper Deck Lining | 192 | Carbon Steel | W10x45# WF | 4.32 | 1540 | ton | 6652.8 | 1.6667 | 3.5196 | 39025.3248
Lower and Upper Deck Lining | 640 | Carbon Steel | W10x45# WF | 14.4 | 1540 | ton | 22176 | 1.6667 | 3.5196 | 130084.416
Tube Bundle Shop Fabrication | 15 | 316L SS | 90/10 CuNi |  | 477528.75 | each | 7162931.25 | 1.6667 | 3.5196 | 42017754.7125
Nozzles, Manholes | 25 | 316L SS | 316L SS | 25 | 2666.67 | each | 66666.75 | 1.6667 | 3.5196 | 391067.1555
Paint |  | Blast Sand | Epoxy |  |  |  | 70000 | 1.6667 | 3.5196 | 410620
Insulation / Lagging | 6664 | Fiberglass | Aluminum | 6664 | 10 | each | 66640 | 1.6667 | 3.5196 | 390910.24
Platform, Stairs, Railing | 1133.3333 |  |  | 1133.3333 | 100 | each | 113333.3333 | 1.6667 | 3.5196 | 664813.3333
Evaporator Total |  |  |  | 1620.365 |  |  | 13597544.9133 |  |  | 79763198.4616
Deaerator | 31 | 316L SS | 316L SS | 8 | 4420 | ton | 35360 | 1 | 3.5196 | 124453.056

## 20MGD 60 Effect Levellized VTE
20 MGD 60 Effect VTE-MED | Amount | Unit
Plant capital cost | 51156410.5807 | each plant
Amortizaton period | 30 | years
Interest rate | 8% | per year
Plant life capital cost | 135132342.5195
Annualized capital cost | 4504411.4173 |  | 0.17158
Performance Ratio | 56 | lbs/1,000 BTU
Distillate capacity | 20000000 | gpd | 75708.2507 | m3/day
Distillate capacity | 75708.2507 | m3/day
Concentration factor | 5
Brine Capacity | 4000000 | gpd
Recovery ratio | 83.33%
Plant availability | 95%
Plant spec cost | 2.5578
Plant Operating Costs
Electrical requirement | 1579.2674 | KW
Electrical rate | 0.085 | per kWh
Electrical cost | 1117126.3804 | per year
Thermal requirement @392°F | 120000 | lbs/hr
Thermal rate (geothermal) | 0.0045 | per lb/hr
Thermal cost (geothermal) | 4493880 | per year
Thermal requirement | 100068000 | BTU/hr
Thermal requirement | 29327.0358 | kWt
Annual Energy Cost | 5611006.3804
Operation & maintenance | 3723000 | per year
Chemicals | 438000 | per year
Maintenance Supplies | 146000 | per year
Annual O&M Cost | 4307000
Annualized Plant Cost | 14422417.7977
Distillate cost | 2.0797 | per 1,000 gal
Distillate cost | 0.54939 | per m3
Distillate cost | 677.6631 | per acre-ft
Amortized Capital Cost | 0.17158 | per m3
Annual Distillate Output | 21282.5778 | AFY
Annual Brine Output | 4256.5156 | AFY
Annual Salt in Brine Output | 1368760.2022 | metric tons
Enthalpy of Evaporation | 833.9 | Btu/lb
Thermal Use per m3 | 9.2969 | kWht/m3
Electrical Use per m3 | 0.50064 | kWh/m3

## 20MGD 60Effect VTE Capital Cost
20 MGD 60 Effect VTE-MED | Capital Cost
Evaporator 60 effects | 26869167.92
Deaerator | 35360
Foundation | 37925.9259
Excavation | 13333.3333
Chemical feed system | 20000
Pumps and Motors | 1751840.9438
Steam ejector system | 50000
Piping and valves | 1200000
Electrical gear & cables | 1000000
Instrumentation | 400000
Computer control sytem | 50000
Misc. bolts, nuts, gaskets | 40000
Subtotal Construction Equipment & Materials | 31467628.123
Freight in (1.5% of materials) | 472014.4218
Insurance (0.5% of materials) | 157338.1406
Mobilization | 167000
Installation & site fabrication | 734000
Subtotal Construction Contract | 1530352.5625
Contractor markup (15% of above) | 4949697.1028
Total Construction Contract | 37947677.7883
Materials inspection (1.5% of materials) | 472014.4218
Construction management (5% of contract) | 1897383.8894
Design & engineering (8% of contact) | 3035814.2231
Total Plant Costs | 43352890.3227
Interest during construction (8% of total) | 3468231.2258
Contingencies (10% of total) | 4335289.0323
Total Plant Construction Project | 51156410.5807

## 20MGD 60Effect VTE Excavation
Description | Amount 1 | Unit | Amount 2 | Unit | Total Amount | Unit | Unit Cost | Unit | Cost
Demister Screens 316 SS | 1800 | ft² | 4 | inch | 600 | ft³ | 106 | ft³ | 63600
Foundation | 8 | each | 320 | ft³ | 94.8148 | yd³ | 400 | yd³ | 37925.9259
Excavation | 8 | each | 900 | ft³ | 266.6667 | yd³ | 50 | yd³ | 13333.3333

## 20MGD 60Effect Pump Specs
Pump | Quantity | Flow Rate | Head | SG | Eff | HP | Total HP
|  | (gpm) | (ft)
Brine Recycle | 12 | 4342 | 80 | 1.2 | 75% | 140.3475 | 1684.1697
Feed (DA) | 1 | 4342 | 90 | 1.03 | 82% | 123.954 | 123.954
Distillate | 1 | 3472 | 35 | 1 | 78% | 39.3421 | 39.3421
Brine Blowdown | 1 | 870 | 35 | 1.2 | 65% | 14.1958 | 14.1958
Condensate | 1 | 260 | 35 | 1 | 72% | 3.1916 | 3.1916
Seawater In | 1 | 8500 | 50 | 1.03 | 84% | 131.5987 | 131.5987
Coolant | 1 | 10000 | 35 | 1.03 | 75% | 121.3805 | 121.3805
Total HP | [6 empty] | 2117.8325
Total KW | [6 empty] | 1579.2674
Material for all |  | Ni Resist
Impeller |  | 316L SS
Seals |  | Mechanical
Frequency |  | 60 Hz
Pump base |  | common

## 20MGD 60Effect Evaporator Cost
Evaporator Components | Volume of | Material | Material | Weight | Unit Cost | Unit | 15-60 effect | Cost
60 Effect 20 MGD VTE-MED | (ft³) |  |  | (tons) |  |  | multiplier
Lower and Upper Deck | 698 | A285 grade C | A516 grade 70 | 171.01 | 1600 | ton | 4 | 1094464
Sidewalls | 140 | A285 grade C | A516 grade 70 | 34.3 | 1600 | ton | 4 | 219520
Endwalls | 24 | A285 grade C | A516 grade 70 | 5.88 | 1600 | ton | 4 | 37632
Endwall Chamfer | 8 | A285 grade C | A516 grade 70 | 1.96 | 1600 | ton | 4 | 12544
Lower and Upper Deck Lining | 116.3 | 316L SS | 316L SS | 29.075 | 4420 | ton | 4 | 514046
Sidewalls Lining | 4 | 316L SS | 316L SS | 1 | 4420 | ton | 4 | 17680
Endwall lining | 2 | 316L SS | 316L SS | 0.5 | 4420 | ton | 4 | 8840
Endwall Chamfer Lining | 1 | 316L SS | 316L SS | 0.25 | 4420 | ton | 4 | 4420
Effect Cylinder | 1433 | 316L SS | 316L SS | 358.25 | 4420 | ton | 4 | 6333860
Effect Cylinder Cover | 147 | 316L SS | 316L SS | 36.75 | 4420 | ton | 4 | 649740
Effect Bottom Cone | 110 | 316L SS | 316L SS | 27.5 | 4420 | ton | 4 | 486200
Tubesheet | 2160 | 316L SS | 316L SS | 540 | 4420 | ton | 4 | 9547200
Tubes | 1320 | 3" | Aluminum | 331.32 | 3454 | ton | 4 | 4577517.12
Demister | 360 | Mesh | 316L SS | 3 | 21600 | ton | 4 | 259200
(ft)
Beams, Lower and Upper Deck | 1860 | Carbon Steel | W10x45# WF | 41.85 | 1540 | ton | 4 | 257796
Lower and Upper Deck Lining | 192 | Carbon Steel | W10x45# WF | 4.32 | 1540 | ton | 4 | 26611.2
Lower and Upper Deck Lining | 384 | Carbon Steel | W10x45# WF | 8.64 | 1540 | ton | 4 | 53222.4
Tube Bundle Shop Fabrication | 15 | 316L SS | 90/10 CuNi | 1 | 477528.75 | each | 4 | 1910115
Nozzles, Manholes | 15 | 316L SS | 316L SS | 15 | 2666.67 | each | 4 | 160000.2
Paint |  | Blast Sand | Epoxy | 1 | 40000 |  | 4 | 160000
Insulation / Lagging | 6664 | Fiberglass | Aluminum | 6664 | 10 | each | 4 | 266560
Platform, Stairs, Railing | 680 |  |  | 680 | 100 | each | 4 | 272000
Evaporator Total |  |  |  | 1595.605 |  |  |  | 26869167.92
Deaerator | 31 | 316L SS | 316L SS | 8 | 4420 | ton |  | 35360

## 20MGD Adjacent Tube Bundle
Item | Quantity | Unit
Number of Effects (w/o condenser) | 15
Tube Length | 30 | ft
Tubes per Effect | 1340
Effect Area | 31578 | ft2
Tube Bundle Diameter | 12 | ft
Total Vessel Height | 40 | ft
Tube Vessel Width | 13 | ft
Separation Vessel Width | 18 | ft
Demister Area per Effect | 120 | ft2
Tube Diameter | 3 | inches
Vessel Material
Vessel Cladding
Tube Material (double fluted) E2-15 | 90/10 CuNi | Alternative to be tested, Aluminum Brass
Tube Material (smooth or fluted) E1 | Ti | Alternatives to be evaluated, double fluted 90/10 CuNi or Aluminum Brass
Vertical Tube Condenser
Number of Bundles per Unit | 1
Tube Length | 30 | ft
Tubes per Bundle | 4020
Heat Transfer Area | 94719.0185 | ft2
Tube Bundle Diameter | 12 | ft
Total Vessel Height | 70 | ft
Tube Vessel Width | 13 | ft
Overall Vessel Width | 13 | ft
Tube Diameter | 1 | inch
Tube Material (smooth) | 90/10 CuNi | Alternative, Naval Bronze

## 20 MGD Stacked Tube Bundle
Stacked VTE-MED Configuration | Quantity | Unit
Evaporator Specifications
Number of Effects per Stack | 5 | per stack
Number of Bundles per Effect | 3 | per effect
Number Of Tube Bundles per Unit | 15 | per unit
Tube Length | 10 | ft
Tubes per Effect | 1340
Effect Area | 31578 | ft2
Tube Bundle Diameter | 12 | ft
Vessel Height | 70 | ft
Bundle Insert Width | 13 | ft
Overall Vessel Width | 54 | ft
Demister Area per Effect | 360 | ft2
Tube Diameter | 3 | inches
Tube Material (double fluted) E2-15 | 90/10 CuNi | Alternative to be tested: Aluminum Brass
Tube Material (smooth or fluted) E1 | Ti | Alternatives to be evaluated:
double fluted 90/10 CuNi or Aluminum Brass
Vertical Tube Condenser/Heater
Number of Bundles per Unit | 2
Tube Length (straight tubes) | 60 | ft
Tubes per Bundle | 1340
Heat Transfer Area per Bundle | 63146.0123 | ft2
Tube Bundle Diameter | 12 | ft
Vessel Height | 70 | ft
Bundle Insert Width | 13 | ft
Overall Vessel Width | 54 | ft
Tube Diameter | 1 | inch
Tube Material (smooth or fluted) | 90/10 CuNi | Alternative, Naval Bronze

## 14MGD 40 Effect Levellized VTE
Description | Cost | Unit
Plant capital cost | 37580651.4558 | each
Amortizaton period | 30 | years
Interest rate | 8.3% | per year
Plant life capital cost | 102115061.8835
Annualized capital cost | 3403835.3961 |  | 0.18618
Distillate capacity | 13928571 | gpd | 52725.3872 | m3/day
Concentration factor | 12
Brine Capacity | 1160714.25 | gpd
Recovery ratio | 92.31%
Plant availability | 95%
Plant spec cost | 2.6981
Plant Operating Costs
Electrical requirement | 2678.1669 | KW
Electrical rate | 0.085 | per kWh
Electrical cost | 1894454.9102 | per year
Thermal requirement | 120000 | lbs/hr
Thermal rate (geothermal) | 0.0045 | per lb/hr | 0.0045
Thermal cost (geothermal) | 4493880 | per year
Thermal requirement | 100068000 | BTU/hr
Thermal requirement | 29327.0358 | kWt
Thermal rate (solar) | 0.01 | kWht
Thermal cost (solar) | 2440595.9234 | per year
Annual Energy Cost | 4335050.8336
Operation & maintenance | 2592803.4917 | per year
Chemicals | 305035.7049 | per year
Maintenance Supplies | 101678.5683 | per year
Annual O&M Cost | 7334568.5985
Annualized Plant Cost | 10738403.9946
Distillate cost | 2.2234 | per 1,000 gal
Distillate cost | 0.58736 | per m3
Distillate cost | 724.5009 | per acre-ft
Amortized Capital Cost | 0.18618 | per m3
Annual Distillate Output | 14821.7948 | AFY
Enthalpy of Evaporation | 833.9 | Btu/lb
Thermal Use per m3 | 13.3493 | kWht/m3
Electrical Use per MG | 192.2787 | kWh/MG

## 14MGD 40Effect VTE Capital Cost
Description | Cost
Evaporator 40 effect | 17912778.6133
Deaerator | 35360
Foundation | 47407.4074
Excavation | 16666.6667
Chemical feed system | 20000
Pumps and Motors | 2970822.0449
Steam ejector system | 50000
Piping and valves | 810000
Electrical gear & cables | 675000
Instrumentation | 270000
Computer control sytem | 50000
Misc. bolts, nuts, gaskets | 27000
Subtotal Construction Equipment & Materials | 22885034.7323
Freight in (1.5% of materials) | 343275.521
Insurance (0.5% of materials) | 114425.1737
Mobilization | 167000
Installation & site fabrication | 734000
Subtotal Construction Contract | 1358700.6946
Contractor markup (15% of above) | 3636560.314
Total Construction Contract | 27880295.741
Materials inspection (1.5% of materials) | 343275.521
Construction management (5% of contract) | 1394014.787
Design & engineering (8% of contact) | 2230423.6593
Total Plant Costs | 31848009.7083
Interest during construction (8% of total) | 2547840.7767
Contingencies (10% of total) | 3184800.9708
Total Plant Construction Project | 37580651.4558

## 14MGD 40Effect VTE Excavation
Description | Amount 1 | Unit | Amount 2 | Unit | Total Amount | Unit | Unit Cost | Unit | Cost
Demister Screens 316 SS | 1800 | ft² | 4 | inch | 600 | ft³ | 106 | ft³ | 63600
Foundation | 10 | each | 320 | ft³ | 118.5185 | yd³ | 400 | yd³ | 47407.4074
Excavation | 10 | each | 900 | ft³ | 333.3333 | yd³ | 50 | yd³ | 16666.6667

## 14MGD 40Effect Pump Specs
Pump | Quantity | Flow Rate | Head | SG | Eff | HP | Total HP
|  | (gpm) | (ft)
Brine Recycle | 40 | 4342 | 45 | 1.2 | 75% | 78.9455 | 3157.8182
Feed (DA) | 1 | 4342 | 90 | 1.03 | 82% | 123.954 | 123.954
Distillate | 1 | 3472 | 35 | 1 | 78% | 39.3421 | 39.3421
Brine Blowdown | 1 | 870 | 35 | 1.2 | 65% | 14.1958 | 14.1958
Condensate | 1 | 260 | 35 | 1 | 72% | 3.1916 | 3.1916
Seawater In | 1 | 8500 | 50 | 1.03 | 84% | 131.5987 | 131.5987
Coolant | 1 | 10000 | 35 | 1.03 | 75% | 121.3805 | 121.3805
Total HP | [6 empty] | 3591.481
Total KW | [6 empty] | 2678.1669
Material for all |  | Ni Resist
Impeller |  | 316L SS
Seals |  | Mechanical
Frequency |  | 60 Hz
Pump base |  | common

## 14MGD 40Effect Evaporator Cost
Evaporator Components | Volume of | Material | Material | Weight | Unit Cost | Unit | 40 effect scale | Cost
| (ft³) |  |  | (tons)
Lower and Upper Deck | 698 | A285 grade C | A516 grade 70 | 171.01 | 1600 | ton | 2.6667 | 729642.6667
Sidewalls | 140 | A285 grade C | A516 grade 70 | 34.3 | 1600 | ton | 2.6667 | 146346.6667
Endwalls | 24 | A285 grade C | A516 grade 70 | 5.88 | 1600 | ton | 2.6667 | 25088
Endwall Chamfer | 8 | A285 grade C | A516 grade 70 | 1.96 | 1600 | ton | 2.6667 | 8362.6667
Lower and Upper Deck Lining | 116.3 | 316L SS | 316L SS | 29.075 | 4420 | ton | 2.6667 | 342697.3333
Sidewalls Lining | 4 | 316L SS | 316L SS | 1 | 4420 | ton | 2.6667 | 11786.6667
Endwall lining | 2 | 316L SS | 316L SS | 0.5 | 4420 | ton | 2.6667 | 5893.3333
Endwall Chamfer Lining | 1 | 316L SS | 316L SS | 0.25 | 4420 | ton | 2.6667 | 2946.6667
Effect Cylinder | 1433 | 316L SS | 316L SS | 358.25 | 4420 | ton | 2.6667 | 4222573.3333
Effect Cylinder Cover | 147 | 316L SS | 316L SS | 36.75 | 4420 | ton | 2.6667 | 433160
Effect Bottom Cone | 110 | 316L SS | 316L SS | 27.5 | 4420 | ton | 2.6667 | 324133.3333
Tubesheet | 2160 | 316L SS | 316L SS | 540 | 4420 | ton | 2.6667 | 6364800
Tubes | 1320 | 3" | Aluminum | 331.32 | 3454 | ton | 2.6667 | 3051678.08
Demister | 360 | Mesh | 316L SS | 3 | 21600 | ton | 2.6667 | 172800
(ft)
Beams, Lower and Upper Deck | 1860 | Carbon Steel | W10x45# WF | 41.85 | 1540 | ton | 2.6667 | 171864
Lower and Upper Deck Lining | 192 | Carbon Steel | W10x45# WF | 4.32 | 1540 | ton | 2.6667 | 17740.8
Lower and Upper Deck Lining | 384 | Carbon Steel | W10x45# WF | 8.64 | 1540 | ton | 2.6667 | 35481.6
Tube Bundle Shop Fabrication | 15 | 316L SS | 90/10 CuNi | 1 | 477528.75 | each | 2.6667 | 1273410
Nozzles, Manholes | 15 | 316L SS | 316L SS | 15 | 2666.67 | each | 2.6667 | 106666.8
Paint |  | Blast Sand | Epoxy | 1 | 40000 |  | 2.6667 | 106666.6667
Insulation / Lagging | 6664 | Fiberglass | Aluminum | 6664 | 10 | each | 2.6667 | 177706.6667
Platform, Stairs, Railing | 680 |  |  | 680 | 100 | each | 2.6667 | 181333.3333
Evaporator Total |  |  |  | 1595.605 |  |  |  | 17912778.6133
Deaerator | 31 | 316L SS | 316L SS | 8 | 4420 | ton |  | 35360

## 14MGD Adjacent Tube Bundle
Item | Quantity | Unit
Number of Effects (w/o condenser) | 40
Tube Length | 30 | ft
Tubes per Effect | 1340
Effect Area | 84208 | ft2
Tube Bundle Diameter | 12 | ft
Total Vessel Height | 40 | ft
Tube Vessel Width | 13 | ft
Separation Vessel Width | 18 | ft
Demister Area per Effect | 120 | ft2
Tube Diameter | 3 | inches
Vessel Material
Vessel Cladding
Tube Material (double fluted) E2-15 | 90/10 CuNi | Alternative to be tested, Aluminum Brass
Tube Material (smooth or fluted) E1 | Ti | Alternatives to be evaluated, double fluted 90/10 CuNi or Aluminum Brass
Vertical Tube Condenser
Number of Bundles per Unit | 1
Tube Length | 30 | ft
Tubes per Bundle | 4020
Heat Transfer Area | 94719.0185 | ft2
Tube Bundle Diameter | 12 | ft
Total Vessel Height | 70 | ft
Tube Vessel Width | 13 | ft
Overall Vessel Width | 13 | ft
Tube Diameter | 1 | inch
Tube Material (smooth) | 90/10 CuNi | Alternative, Naval Bronze

## 5MGD 15 Effect Levellized VTE
Levellized Cost Estimate | Cost | Unit
15 Effect 5 MGD VTE-MED
Plant capital cost | 25369589.3258 | each
Amortizaton period | 30 | years
Interest rate | 8% | per year
Plant life capital cost | 67015101.2441
Annualized capital cost | 2233836.7081 |  | 0.34037
Distillate capacity | 5000000 | gpd | 18927.0627 | m3/day
Concentration factor | 6.02
Brine Capacity | 830564.7841 | gpd
Recovery ratio | 85.75%
Plant availability | 95%
Plant spec cost | 5.0739
Plant Operating Costs
Electrical requirement | 15296.4853 | kWh/day
Electrical rate | 0.085 | per kWh
Electrical cost | 450844.7835 | per year
Thermal requirement | 120000 | lbs/hr
Thermal rate | 0.0045 | per lb/hr | 0.0045
Thermal cost | 4493880 | per year
Annual Energy Cost | 4944724.7835
Operation & maintenance | 930750 | per year
Chemicals | 109500 | per year
Maintenance Supplies | 36500 | per year
Annual O&M Cost | 6021474.7835
Annualized Plant Cost | 8255311.4916
Distillate cost | 4.7615 | per 1,000 gal
Distillate cost | 1.2579 | per m3
Distillate cost | 1551.5623 | per acre-ft
Annual Distillate Output | 5320.6445 | AFY
Enthalpy of Evaporation | 970 | Btu/lb
Thermal Use per m3 | 43.2568 | kWht/m3
Electrical Use per m3 | 0.80818 | kWh/m3

## 5MGD 15 Effect VTE Capital Cost
15 Effect 5 MGD Design Capital Cost Estimate
Description | Cost
Evaporator 15 effect | 13402694.48
Deaerator | 35360
Foundation | 180148.1481
Excavation | 60000
Chemical feed system | 20000
Pumps and Motors | 707000
Steam ejector system | 50000
Piping and valves | 300000
Electrical gear & cables | 250000
Instrumentation | 100000
Computer control sytem | 50000
Misc. bolts, nuts, gaskets | 10000
Subtotal Construction Equipment & Materials | 15165202.6281
Freight in (1.5% of materials) | 227478.0394
Insurance (0.5% of materials) | 75826.0131
Mobilization | 167000
Installation & site fabrication | 734000
Subtotal Construction Contract | 1204304.0526
Contractor markup (15% of above) | 2455426.0021
Total Construction Contract | 18824932.6828
Materials inspection (1.5% of materials) | 227478.0394
Construction management (5% of contract) | 941246.6341
Design & engineering (8% of contact) | 1505994.6146
Total Plant Costs | 21499651.971
Interest during construction (8% of total) | 1719972.1577
Contingencies (10% of total) | 2149965.1971
Total Plant Construction Project | 25369589.3258

## 5 MGD 15 Effect VTE Excavation
Description | Amount 1 | Unit | Amount 2 | Unit | Total Amount | Unit | Unit Cost | Unit | Cost
Demister Screens 316 SS | 1800 | ft² | 4 | inch | 600 | ft³ | 106 | ft³ | 63600
Foundation | 4 | each | 320 | ft³ | 47.4074 | yd³ | 400 | yd³ | 18962.963
Excavation | 4 | each | 900 | ft³ | 133.3333 | yd³ | 50 | yd³ | 6666.6667

## 5MGD 15 Effect Pump Specs kW
Pump Specifications | Quantity | Flow Rate | Head | SG | Eff | HP | Total HP
15 Effect 5 MGD 3 Stacks |  | (gpm) | (ft)
Brine Recycle | 3 | 4342 | 80 | 1.2 | 75% | 140.3475 | 421.0424
Feed (DA) | 1 | 4342 | 90 | 1.03 | 82% | 123.954 | 123.954
Distillate | 1 | 3472 | 35 | 1 | 78% | 39.3421 | 39.3421
Brine Blowdown | 1 | 870 | 35 | 1.2 | 65% | 14.1958 | 14.1958
Condensate | 1 | 260 | 35 | 1 | 72% | 3.1916 | 3.1916
Seawater In | 1 | 8500 | 50 | 1.03 | 84% | 131.5987 | 131.5987
Coolant | 1 | 10000 | 35 | 1.03 | 75% | 121.3805 | 121.3805
Total HP | [6 empty] | 854.7052
Total KW | [6 empty] | 637.3536
Material for all |  | Ni Resist
Impeller |  | 316L SS
Seals |  | Mechanical
Frequency |  | 60 Hz
Pump base |  | common

## 5MGD 15 Effect Evaporator Costs
Evaporator Components | Volume of | Material | Material | Weight | Unit Cost | Unit | Cost
15 Effect 5 MGD design | (ft³) |  |  | (tons)
Lower and Upper Deck | 698 | A285 grade C | A516 grade 70 | 171.01 | 1600 | ton | 273616
Sidewalls | 140 | A285 grade C | A516 grade 70 | 34.3 | 1600 | ton | 54880
Endwalls | 24 | A285 grade C | A516 grade 70 | 5.88 | 1600 | ton | 9408
Endwall Chamfer | 8 | A285 grade C | A516 grade 70 | 1.96 | 1600 | ton | 3136
Lower and Upper Deck Lining | 116.3 | 316L SS | 316L SS | 29.075 | 4420 | ton | 128511.5
Sidewalls Lining | 4 | 316L SS | 316L SS | 1 | 4420 | ton | 4420
Endwall lining | 2 | 316L SS | 316L SS | 0.5 | 4420 | ton | 2210
Endwall Chamfer Lining | 1 | 316L SS | 316L SS | 0.25 | 4420 | ton | 1105
Effect Cylinder | 1433 | 316L SS | 316L SS | 358.25 | 4420 | ton | 1583465
Effect Cylinder Cover | 147 | 316L SS | 316L SS | 36.75 | 4420 | ton | 162435
Effect Bottom Cone | 110 | 316L SS | 316L SS | 27.5 | 4420 | ton | 121550
Tubesheet | 2160 | 316L SS | 316L SS | 540 | 4420 | ton | 2386800
Tubes | 1320 | 3" | Aluminum | 331.32 | 3454 | ton | 1144379.28
Demister | 360 | Mesh | 316L SS | 3 | 21600 | ton | 64800
(ft)
Beams, Lower and Upper Deck | 1860 | Carbon Steel | W10x45# WF | 41.85 | 1540 | ton | 64449
Lower and Upper Deck Lining | 192 | Carbon Steel | W10x45# WF | 4.32 | 1540 | ton | 6652.8
Lower and Upper Deck Lining | 384 | Carbon Steel | W10x45# WF | 8.64 | 1540 | ton | 13305.6
Tube Bundle Shop Fabrication | 15 | 316L SS | 90/10 CuNi |  | 477528.75 | each | 7162931.25
Nozzles, Manholes | 15 | 316L SS | 316L SS | 15 | 2666.67 | each | 40000.05
Paint |  | Blast Sand | Epoxy |  |  |  | 40000
Insulation / Lagging | 6664 | Fiberglass | Aluminum | 6664 | 10 | each | 66640
Platform, Stairs, Railing | 680 |  |  | 680 | 100 | each | 68000
Evaporator Total |  |  |  | 1595.605 |  |  | 13402694.48
Deaerator | 31 | 316L SS | 316L SS | 8 | 4420 | ton | 35360

## 5 MGD Adjacent Tube Bundle Spec
Item | Quantity | Unit
Number of Effects (w/o condenser) | 15
Tube Length | 30 | ft
Tubes per Effect | 1340
Effect Area | 31578 | ft2
Tube Bundle Diameter | 12 | ft
Total Vessel Height | 40 | ft
Tube Vessel Width | 13 | ft
Separation Vessel Width | 18 | ft
Demister Area per Effect | 120 | ft2
Tube Diameter | 3 | inches
Vessel Material
Vessel Cladding
Tube Material (double fluted) E2-15 | 90/10 CuNi | Alternative to be tested, Aluminum Brass
Tube Material (smooth or fluted) E1 | Ti | Alternatives to be evaluated, double fluted 90/10 CuNi or Aluminum Brass
Vertical Tube Condenser
Number of Bundles per Unit | 1
Tube Length | 30 | ft
Tubes per Bundle | 4020
Heat Transfer Area | 94719.0185 | ft2
Tube Bundle Diameter | 12 | ft
Total Vessel Height | 70 | ft
Tube Vessel Width | 13 | ft
Overall Vessel Width | 13 | ft
Tube Diameter | 1 | inch
Tube Material (smooth) | 90/10 CuNi | Alternative, Naval Bronze

## 10 MGD Stacked Tube Bundle Spec
Item | Quantity | Unit
Evaporator
Number of Effects per Stack | 5 | per stack
Number of Bundles per Effect | 5 | per effect
Number Of Tube Bundles per Unit | 25 | per unit
Tube Length | 10 | ft
Tubes per Effect | 1340
Effect Area | 10526 | ft2
Tube Bundle Diameter | 12 | ft
Vessel Height | 70 | ft
Bundle Insert Width | 13 | ft
Overall Vessel Width | 54 | ft
Demister Area per Effect | 600 | ft2
Tube Diameter | 3 | inches
Tube Material (double fluted) E2-5 | 90/10 CuNi | Alternative to be tested, Aluminum Brass
Tube Material (smooth or fluted) E1 | Ti | Alternatives to be evaluated, double fluted 90/10 CuNi or Aluminum Brass
Vertical Tube Condenser/Heater
Number of Bundles per Unit | 2
Tube Length (straight tubes) | 60 | ft
Tubes per Bundle | 1340
Heat Transfer Area per Bundle | 63146.0123 | ft2
Tube Bundle Diameter | 12 | ft
Vessel Height | 70 | ft
Bundle Insert Width | 13 | ft
Overall Vessel Width | 54 | ft
Tube Diameter | 1 | inch
Tube Material (smooth or fluted) | 90/10 CuNi | Alternative, Naval Bronze

## SGSP Summary
Salinity Gradient Solar Ponds
Capital Cost per square mile | 105962068.798
Power output capacity per square mile (baseload seasonal average) | 9.3762 | MW
Annual power output per square mile | 82135.512 | MWh
Purchase Price of Power | 85 | per MWh
Annual revenue estimate per square mile | 6981518.52
Makeup Water Cost (internally produced from Salton Sea) | 0 | per AF
Brine Cost (free from salt extraction reject and VTE) | 0
Annual Operation and Maintenence Cost per square mile | 2472183.6299
Annual Net Income | 4509334.8901
Duration of Power Purchase Agreement (PPA) | 25 | years
Total return on fixed PPA | 112733372.2514
Annual return on fixed PPA | 0.2367%
Transmission Cost
California ISO Wheeling Rate | 8.9873 | per MWh
IID Wheeling Rate | 1096 | per MW/month
IID Wheeling Rate (baseload) | 1.5014 | per MWh

## SGSP Section Cost low evap.
Item |  | Permits (1yr) | Construction (1yr) | Operation (1yr) | Plant Life Cost (30yr)
Pond Construction manager |  | 100000 | 100000 | 0 | 200000 |  | Personnel | 660000 | 518333.3333 | 1110000 | 34478333.3333
Chemical/Process Engineer |  | 150000 | 75000 | 0 | 225000
Mechanical Engineer |  | 150000 | 75000 | 0 | 225000
Civil Engineer |  | 150000 | 75000 | 0 | 225000
Pond Operations Manager |  | 100000 | 100000 | 100000 | 3200000
Pond and Plant Operators (8) |  | 0 | 40000 | 480000 | 14440000
Equipment Maintenance Techs (4) |  | 0 | 26666.6667 | 320000 | 9626666.6667
On site Lab Techs (4) |  | 0 | 16666.6667 | 200000 | 6016666.6667
Accounting Service |  | 10000 | 10000 | 10000 | 320000
Permit documentation and fees |  | 100000 | 50000 | 1000 | 180000 |  | Permits/Insurance | 140000 | 200000 | 151000 | 4870000
Pollution liability insurance |  | 0 | 110000 | 110000 | 3410000
Commercial general liability insurance |  | 40000 | 40000 | 40000 | 1280000
Power generation equipment (rent) |  | 0 | 356800 | 0 | 356800 |  | Pond Construction | 0 | 31733456 | 260536.96 | 39549564.8
Site lighting |  | 0 | 80000 | 2400 | 152000
Dike material aquisition (IID Quarry?) |  | 0 | 6400000 | 0 | 6400000
In Sea dike construction and maintenance |  | 0 | 15469696 | 154696.96 | 20110604.8 |  | 36638.525
Pump out ponds inside dikes |  | 0 | 160000 | 0 | 160000
Muck out ponds |  | 0 | 1418960 | 0 | 1418960
Construction piping |  | 0 | 320000 | 0 | 320000
Run power to pond pumps |  | 0 | 640000 | 0 | 640000
Site communications |  | 0 | 40000 | 10000 | 340000
Construction Equipment Rental |  | 0 | 1600000 | 0 | 1600000
Install and maintain pond piping |  | 0 | 3200000 | 32000 | 4160000
Install and maintain pond pumps |  | 0 | 2048000 | 61440 | 3891200
Install and maintain ORC engines (10 MW) |  | 0 | 12156000 | 364680 | 23096400 |  | Electric Generation | 0 | 14556000 | 388680 | 26216400
Install and maintain power transmission (10 MW) |  | 0 | 2400000 | 24000 | 3120000
Install and maintain seawater intake |  | 0 | 1231325 | 36939.75 | 2339517.5 |  | Water Treatment | 0 | 7700837.3314 | 499326.6699 | 22680637.4297
Install and maintain seawater distillation equipment |  | 0 | 6342397.3314 | 190271.9199 | 12050554.9297
Water treatment chemicals |  | 0 | 60000 | 120000 | 3660000
Pond film and recharge (Cover Free) |  | 0 | 67115 | 67115 | 2080565
Seawater Water Make-up Pumping (AFY) | 1700 | 0 | 0 | 85000 | 2550000
Pond liner purchase (hi-temperature) |  | 0 | 40256000 | 0 | 40256000 |  | Pond Liner | 0 | 42214000 | 0 | 42214000
Pond liner installation support (hi-temperature) |  | 0 | 1600000 | 0 | 1600000
Pipe penetration boots |  | 0 | 358000 | 0 | 358000
Metal storage sheds |  | 0 | 128000 | 3840 | 243200 |  | Infrastructure | 13600 | 376800 | 62640 | 2269600
Transportation (truck rentals) |  | 10000 | 120000 | 10000 | 430000
Shop equiptment |  | 0 | 100000 | 20000 | 700000
Small Tools & Supplies |  | 3600 | 28800 | 28800 | 896400
Working Cash |  | 65088 | 7783954.1332 |  | 7849042.1332 |  | Working Cash | 65088 | 7783954.1332 | 0 | 7849042.1332
Sub total |  | 878688 | 105083380.798 | 2472183.6299 | 180127577.6963 |  | 180127577.6963 | 878688 | 105083380.798 | 2472183.6299 | 180127577.6963
Construction Bond period (years) | 30
Construction Bond Annual Interest Rate | 4%
Montly Loan Payment |  | 4194.9909 | 505879.1238 | 505879.1238
Construction Financing Total @ 4.5% for 30 years |  | 50339.8909 | 6070549.486 | 6070549.486 | 182116484.5799
Total |  | 929027.8909 | 111153930.284 | 8542733.1159 | 256281993.4782
Percentage of thermal capacity for thermal distillation | 25%
Average electrical output kW/ 5 acres | 78.135 |  |  | 9376.2 |  | 600
Baseload Generation (MW) |  | 0 | 0 | 9.3762
Annual Electricity Output MWh |  | 0 | 0 | 73921.9608 | 2217658.824
Annual Electricity Revenue @ $85/MWh | 85 | 0 | 0 | 6283366.668 | 188501000.04
Net Equity |  | -878688 | -105083380.798 | 3811183.0381 | 8373422.3437
Evaporation loss |  | 75% reduction
Annual avg water use for surface make-up (AFY) | 2181.8912 | 850 |  |  |  |  | 0
Annual avg water production (AFY) |  | 1144.8887
Annual avg water surplus/defecit (AFY) |  | 294.8887
US gal/AF |  | 325853.3837

## SGSP Pond Sizing
Pond Bottom Area | 10 | acres
Pond Bottom Area | 40468.6 | square meters
Pond Berm slope | 2 | to one
LCZ Depth | 2 | meters
NCZ Depth | 1.2 | meters
UCZ Depth | 0.2 | meters
Freeboard | 0.5 | meters
Berm height | 3.9 | meters
Berm height | 12.7953 | feet
Berm run | 7.8 | meters
Square Pond Berm bottom edge | 660 | feet
Square Pond Berm top edge | 685.5906 | feet
Square Pond Berm linear feet | 2742.3622 | feet
Square Pond Berm bottom edge | 201.1681 | meters
Square Pond Berm top edge | 216.7681 | meters
LCZ volume | 82546.5447 | cubic meters
NCZ volume | 53706.3555 | cubic meters
UCZ volume | 9190.7035 | cubic meters

## SGSP Salt content
LCZ Specific Gravity | 1.18
UCZ Specific Gravity | 1.01
Density of water | 1 | tonne/m3
Density of saturated NaCl at 49.93 deg C | 1189200 | mg/liter
Density of LCZ brine | 310000 | mg/liter
Mass percent LCZ if NaCl solution | 26.07%
Density of UCZ brine | 35000 | mg/liter
Mass percent UCZ if NaCl solution | 2.943%
LCZ Salt Content | 25391.4615 | tonnes
NCZ Salt Content | 9058.3184 | tonnes
UCZ Salt Content | 273.2016 | tonnes
Total Salt Content (per pond) | 34722.9816 | tonnes
Pond bottom size | 10 | acres

## Solar Pond Brine Cost
VTE Plant Specs | Amount | Unit | Saturated Brine Cost (600 acre build/yr) | Amount | Unit
Distillate capacity | 5000000 | gpd | Assumptions used for Estimate
Distillate purity (minimum) | 50 | mg/liter
Performance Ratio | 13.7 | lb/1000 Btu | Baseload Capacity (solar ponds) | 10 | MW
Steam Pressure | 3 | psig | Annnual Output (solar ponds) | 8322000 | Mwh/yr
Steam Requirement | 109000 | lb/hr | Unit Energy Cost (solar ponds) | 85 | per MW
Concentration factor | 6.02 |  | Annualized Cost (solar ponds) | 7446000
Brine Capacity | 830564.7841 | gpd
Recovery ratio | 85.75% |  | Distilled Water Cost (distilled water returned to Sea) | 761.4126 | per acre-ft
Plant availability | 90% |  | Distilled Water Rate (distilled water returned to Sea) | 5040.6105 | acre-ft/yr
|  |  | Well Water Cost | 207 | per acre-ft
VTE Plant Costs |  |  | Build Water | 2000 | acre-ft
Plant capital cost | 25369589.3258 | each | Build Water Cost | 414000 | Per 10 MW
Amortizaton period | 25 | years | Pond Makeup Water | 3240.3 | acre-ft/yr
Interest rate | 8% | per year | Annualized Pond Operation Water Cost | 684542.1 | per year
Plant life capital cost | 58352961.816 | 30 years
Annualized capital cost | 2334118.4726 | per year | Saturated Brine Costs
O&M Costs |  |  | Saturated brine cost | 14.0668 | per 1,000 gal
Electrical requirement | 15296.4853 | kWh/day | Saturated brine cost | 4583.7041 | per acre-ft
Electrical rate | 0.085 | per kWh | Brine to Ponds | 6300 | acre-ft/yr
Electrical cost | 427116.1106 | per year | Unit Brine Cost | 4583.7041 | per acre-ft
Operation & maintenance | 930750 | per year | Annual Brine Cost (equals annual VTE plant cost) | 3837984.5833 | per year
Chemicals | 109500 | per year | Unit Energy Cost of brine ($/MWh) | 0.46119 | per MWh
Maintenance Supplies | 36500 | per year
Annual O&M Cost | 1503866.1106 | per year | Salt in Saturated Brine | 310000 | mg/liter
Annualized Plant Cost | 3837984.5833 | per year | Salt in Saturated Brine | 1.1735 | kg/gal
|  |  | Salt in Saturated Brine | 382.3815 | tonne/AF
Distillate cost | 2.3367 | per 1,000 gal | Salt to Ponds | 2409003.3474 | tonne/yr
Distillate cost | 761.4126 | per acre-ft
Saturated brine cost | 14.0668 | per 1,000 gal
Saturated brine cost | 4583.7041 | per acre-ft

## Salt Evaporation Pond Costs
Solar Salt Evaporation Pond Sizing and Costs
Pond Bottom Area | 10 | In acres
Pond Bottom Area | 435600 | square feet
Pond Inside Edge | 660 | feet
Berm Height | 4 | feet
Berm Top Width | 10 | feet
Berm Slope X:1 | 2 | W:H ratio
Berm Base Width | 26 | feet
Berm Cross Section | 72 | square feet
Berm Corner Volume | 69.3333 | cubic yards
Berm Side Volume | 1760 | cubic yards
Total Berm Volume | 7317.3333 | cubic yards
Dirt Fill Unit Cost | 4 | cubic yard
Berm Fill Cost | 29269.3333 | total
EDPM Liner roll width | 30 | feet
EDPM Liner roll length | 100 | feet
EDPM Liner roll cost | 2580 | each
Number of Rolls | 146
Cost of Liner 45 mil | 376680
PVC Liner roll width | 48 | feet
PVC Liner roll length | 102 | feet
PVC Liner roll cost | 2399.04 | each
Number of Rolls | 89
Cost of Liner 20 mil | 213514.56
Canal Bottom Width | 3 | feet
Canal Length | 660 | feet
Canal Bottom Area | 1980 | square feet
Canal Inside Edge | 1980 | feet
Berm Height | 4 | feet
Berm Top Width | 2 | feet
Berm Slope X:1 | 1 | W:H ratio
Berm Base Width | 10 | feet
Berm Cross Section | 24 | square feet
Berm Corner Volume | 8.8889 | cubic yards
Berm Side Volume | 1760 | cubic yards
Total Berm Volume | 7075.5556 | cubic yards
Dirt Fill Unit Cost | 4 | cubic yard
Berm Fill Cost | 28302.2222 | total
Salt Fill Labor Cost per Pond | 5000 | each unit
Capital Cost per pond | 276086.1156
Capital Cost per acre | 27608.6116
Maintenance Cost per acre | 10 | per year
Maintenance Cost per pond | 100 | per year
Harvest cost per acre | 1200 | per year
Harvest Cost per pond | 12000 | per year
Annual operating cost per pond | 17100 | per year
Annual operating cost per acre | 1710 | per year
Density of saturated NaCl at 49.93 deg C | 1189200 | mg/liter
Density of NaCl brine | 300000 | mg/liter
Mass percent NaCl brine | 25.23%
Cubic meters per acre foot | 1233.4892
Liters per acre foot | 1233489.2385
Pond brine capacity | 30 | acre feet
Saturated salt capacity per pond | 44005.9621 | metric tons
Saturated salt capacity per acre | 4400.5962 | metric tons

## Blended Water Cost Summary
VTE Plant Specs | Amount | Unit | Groundwater Costs | Amount | Unit
Distillate capacity | 5000000 | gpd | Wellfield development (IID) | 206.9796 | per acre-ft
Distillate purity (minimum) | 50 | mg/liter | Underrun recharge (IID) | 2.7126 | per acre-ft
Performance Ratio | 13.7 | lb/1000 Btu | Sustained groundwater cost | 209.6922 | per acre-ft
Steam Pressure | 3 | psig
Steam Requirement | 109000 | lb/hr | Blended Water Costs | Amount | Unit
Concentration factor | 6.02 |  | Local water distribution (IID) | 5 | per acre-ft
Brine Capacity | 830564.7841 | gpd | Groundwater TDS | 1000 | mg/liter
Recovery ratio | 85.75% |  | Ratio groundwater/distillate | 2.3333
Plant availability | 90% |  | Local blended water cost | 389.808 | per acre-ft
|  |  | Blended water capacity | 51.1477 | acre-ft/day
VTE Plant Costs |  |  | Blended water capacity | 16802.0351 | acre-ft/yr
Plant capital cost | 25369589.3258 | each | Salton Sea return flow | 17.8932 | acre-ft/day
Amortizaton period | 30 | years | Salton Sea return flow | 5877.9213 | acre-ft/yr
Interest rate | 8% | per year | Salton Sea return cost | 209.6922 | per acre-ft
Plant life capital cost | 66571292.6266 | 30 years | Mitigated blended water cost | 463.1654 | per acre-ft
Annualized capital cost | 2219043.0876 | per year
Electrical requirement | 15296.4853 | kWh/day
Electrical rate | 0.14 | per kWh
Electrical cost | 703485.3587 | per year
Operation & maintenance | 930750 | per year
Chemicals | 109500 | per year
Maintenance Supplies | 36500 | per year
Plant spec cost | 5.0739 | per gpd | IID Interim Water Supply Policy | 25000 | acre-ft/yr
Annual O&M Cost | 1780235.3587 | per year | New blended water supply | 16802.0351 | acre-ft/yr
Annualized Plant Cost | 3999278.4463 | per year | IID Interim Water Supply price | 11360613.9388 | per year
Distillate cost | 2.4349 | per 1,000 gal | New blended water supply cost | 7782121.1838 | per year
Distillate cost | 793.4115 | per acre-ft | New blended water savings | 3578492.7549 | per year

## Blended Water Cost 2013
Levellized blended distillate groundwater cost | Quantity | Avg. TDS | Blend ratio | Development cost | Net water cost | Notes
| (AF/yr) | (mg/liter) |  | ($/AF) | ($/AF)
Best case groundwater TDS
IID Underun 19,000+ AF/yr available | 18383.0682 | 771 | 0 | 3 | 3 | Sources: IID Draft IRP Appendix F pg. 6, Appendix N pg. 26
East Mesa Groundwater & Stored Underrun Pumped | 17507.684 | 1000 | 0 | 207 | 210 | Sources: IID Draft IRP Executive Summary pg. 8, Appendix N pg. 26
Z Drain Tile, Tail, and Spill | 6969.9 | 1090 | 0 | 0 | 0 | Sources: 2010 IID TMDL flow data, Z Drain water analysis
Z Drain with Groundwater, total flow in Z Drain | 24477.584 | 1033.4889 | 2.5119 | 0 | 150.2033 | Sources: IID Draft IRP Appendix G pg. 21
Z Drain Flow to Salton Sea | 12716.184 | 1033.4889 | 0 | 0 | 150.2033 | Sources: 2010 IID TMDL flow data, Z Drain water analysis
Makeup Flow to Salton Sea | 5746.284 | 1033.4889 | 0 | 0 | 210 | Sources: VTE Geothermal Desalination Pilot Project data and estimates, Z Drain water analysis
New Irrigation Drain Water (to blending) | 11761.4 | 1033.4889 | 0 | 0 | 210 | Sources: IID Draft IRP Executive Summary pg. 8, Appendix N pg. 26 and IRWMP Project 42
VTE Plant Seawater Feed | 5746.284 | 50000 | 0 | 5 | 8.457 | Salton Seawater feed needed for 6 fold concentration.
VTE Plant Concentrate | 804.4798 | 300000 | 0 | 0 | 0 | Concentrate goes to fill new Salt Gradient Solar Ponds on playa generating electricity and revenue
VTE Plant Distillate (to blending) | 5040.6 | 20 | 0 | 1551.5623 | 1561.2033 | Sources: VTE Geothermal Desalination Pilot Project data and estimates
Blended Recaimed Water (in lieu of River water) | 16802 | 729.4422 | 2.3333 | 5 | 692.181 | Delivered to geothermal plants, local farms, or habitat in lieu of Colorado River water, exchanged for river water delivered to industry
Salt Inflow to Salton Sea (tons) | 17868.9703
Salt Withdrawn from Salton Sea (tons) | 390655.5414
Beneficial Salt Balance to Salton Sea (tons) | -372786.5712
Worse case groundwater TDS
IID Underun 19,000+ AF/yr available | 18753.5523 | 771 | 0 | 3 | 3 | Sources: IID Draft IRP Appendix F pg. 6, Appendix N pg. 26
East Mesa Groundwater & Stored Underrun Pumped | 17860.526 | 1500 | 0 | 207 | 210 | Sources: IID Draft IRP Executive Summary pg. 8, Appendix N pg. 26
Z Drain Tile, Tail, and Spill | 6969.9 | 1090 | 0 | 0 | 0 | Sources: 2010 IID TMDL flow data, Z Drain water analysis
Z Drain with Groundwater, total flow in Z Drain | 24830.426 | 1323.721 | 2.5625 | 0 | 151.053 | Sources: IID Draft IRP Appendix G pg. 21
Z Drain Flow to Salton Sea | 15589.326 | 1323.721 | 0 | 0 | 151.053 | Sources: 2010 IID TMDL flow data, Z Drain water analysis
Makeup Flow to Salton Sea | 8619.426 | 1323.721 | 0 | 0 | 210 | Sources: VTE Geothermal Desalination Pilot Project data and estimates, Z Drain water analysis
New Irrigation Drain Water (to blending) | 9241.1 | 1323.721 | 0 | 0 | 210 | Sources: IID Draft IRP Executive Summary pg. 8, Appendix N pg. 26 and IRWMP Project 42
VTE Plant Seawater Feed | 8619.426 | 50000 | 0 | 5 | 8.3108 | Salton Seawater feed needed for 6 fold concentration.
VTE Plant Concentrate | 1206.7196 | 300000 | 0 | 0 | 0 | Concentrate goes to fill new Salt Gradient Solar Ponds on playa generating electricity and revenue
VTE Plant Distillate (to blending) | 7560.9 | 20 | 0 | 1551.5623 | 1561.0367 | Sources: VTE Geothermal Desalination Pilot Project data and estimates
Blended Reclaimed Water (in lieu of River water) | 16802 | 737.0465 | 1.2222 | 5 | 930.6965 | Delivered to geothermal plants, local farms, or habitat in lieu of Colorado River water, exchanged for river water delivered to industry
Salt Inflow to Salton Sea (tons) | 28058.2573
Salt Withdrawn from Salton Sea (tons) | 585983.3122
Beneficial Salt Balance to Salton Sea (tons) | -557925.0549
Worst case groundwater TDS
IID Underun 19,000+ AF/yr available | 18951.1438 | 771 | 0 | 3 | 3 | Sources: IID Draft IRP Appendix F pg. 6, Appendix N pg. 26
East Mesa Groundwater & Stored Underrun Pumped | 18048.7084 | 2000 | 0 | 207 | 210 | Sources: IID Draft IRP Executive Summary pg. 8, Appendix N pg. 26
Z Drain Tile, Tail, and Spill | 6969.9 | 1090 | 0 | 0 | 0 | Sources: 2010 IID TMDL flow data, Z Drain water analysis
Z Drain with Groundwater, total flow in Z Drain | 25018.6084 | 1573.3721 | 2.5895 | 0 | 151.4964 | Sources: IID Draft IRP Appendix G pg. 21
Z Drain Flow to Salton Sea | 17121.6684 | 1573.3721 | 0 | 0 | 151.4964 | Sources: 2010 IID TMDL flow data, Z Drain water analysis
Makeup Flow to Salton Sea | 10151.7684 | 1573.3721 | 0 | 0 | 210 | Sources: VTE Geothermal Desalination Pilot Project data and estimates, Z Drain water analysis
New Irrigation Drain Water (to blending) | 7896.94 | 1573.3721 | 0 | 0 | 210 | Sources: IID Draft IRP Executive Summary pg. 8, Appendix N pg. 26 and IRWMP Project 42
VTE Plant Seawater Feed | 10151.7684 | 50000 | 0 | 5 | 8.2667 | Salton Seawater feed needed for 6 fold concentration.
VTE Plant Concentrate | 1421.2476 | 300000 | 0 | 0 | 0 | Concentrate goes to fill new Salt Gradient Solar Ponds on playa generating electricity and revenue
VTE Plant Distillate (to blending) | 8905.06 | 20 | 0 | 1551.5623 | 1560.9863 | Sources: VTE Geothermal Desalination Pilot Project data and estimates
Blended Reclaimed Water (in lieu of River water) | 16802 | 750.0849 | 0.88679 | 5 | 1057.9048 | Delivered to geothermal plants, local farms, or habitat in lieu of Colorado River water, exchanged for river water delivered to industry
Salt Inflow to Salton Sea (tons) | 36628.1024
Salt Withdrawn from Salton Sea (tons) | 690158.1232
Beneficial Salt Balance to Salton Sea (tons) | -653530.0208

## IID Cost Basis 2013
Sources: IID Draft IRP Appendix N pg. 26 |  | Sources: IID Draft IRP Appendix N pg. 26 | w/ 6.4% inflation
Wellfield Costs |  | Wellfield Costs
Direct Capital Costs (original sources) |  | Direct Capital Costs (adjusted to 2013)
Ultrafiltration Plant (2001) | 0 | Source Water Development (2013) | 33682406.408
Source Water Development (2009) | 31656397 | Working Capital (2 months of O&M costs) | 426811.896
Recharge Facilities (2009) | 0 | Direct Capital Costs (adjusted to 2011) | 34109218.304
Cooling Blowdown or Seawater Distillation Plant (2009) | 0
Mitigation Costs (reduced flow from drains 2009) | 0 | Indirect Capital Costs
Product Water Distribution (2009) | 0 | Freight and Insurance, 5% of direct capital cost | 1705460.9152
Working Capital (2 months of O&M costs) | 401139 | Owner's direct expense, 10% of direct capital cost | 3410921.8304
Direct Capital Costs (old) | 32057536 | Construction Overhead, 15% of direct capital cost | 5116382.7456
|  | Interest During Construction (1/2 of period 6% rate) | 1023276.5491
Indirect Capital Costs |  | Indirect Capital Costs | 11256042.0403
Freight and Insurance, 5% of direct capital cost | 1582819.85
Owner's direct expense, 10% of direct capital cost | 3205753.6 | Capital Cost | 45365260.3443
Construction Overhead, 15% of direct capital cost | 4808630.4
Interest During Construction (1/2 of period 6% rate) | 961726.08 | Annual O&M costs Wellfield (2013) | 2548103.376
Indirect Capital Costs | 10558929.93 | Annual O&M costs Drain Delivery (2013) | 12768
Capital Cost | 42616465.93 | Financial Analysis - cost per acre foot
|  | Equivalent Annual Cost (4% bond financed) | 5174490.2285
Annual O&M costs Wellfield (2009) | 2394834 | Product Water, acre - feet | 25000
Annual O&M costs Drain Delivery (2009) | 12000 | Equivalent annual cost per acre foot | 206.9796
Financial Analysis - cost per acre foot |  | Sources: IID Draft IRP Appendix N pg. 26 | w/ 6.4% inflation
Equivalent Annual Cost | 4862615.9163
Product Water, acre - feet | 25000 | Recharge Costs
Equivalent annual cost per acre foot | 194.5046 | Direct Capital Costs (adjusted to 2013)
|  | Recharge Facilities (2013) | 444326.4
Sources: IID Draft IRP Appendix N pg. 26 |  | Working Capital (2 months of O&M costs) | 5556.9173
|  | Direct Capital Costs (adjusted to 2013) | 449883.3173
Recharge Costs
Direct Capital Costs (original sources) |  | Indirect Capital Costs
Ultrafiltration Plant (2001) | 0 | Freight and Insurance, 5% of direct capital cost | 22494.1659
Source Water Development (2009) | 0 | Owner's direct expense, 10% of direct capital cost | 44988.3317
Recharge Facilities (2009) | 417600 | Construction Overhead, 15% of direct capital cost | 67482.4976
Cooling Blowdown or Seawater Distillation Plant (2009) | 0 | Interest During Construction (1/2 of period 6% rate) | 13496.4995
Mitigation Costs (reduced flow from drains 2009) | 0 | Indirect Capital Costs | 148461.4947
Product Water Distribution (2009) | 0
Working Capital (2 months of O&M costs) | 5222.6667 | Capital Cost | 598344.8121
Direct Capital Costs (old) | 422822.6667
|  | Annual O&M costs Recharge (2013) | 33341.504
Indirect Capital Costs
Freight and Insurance, 5% of direct capital cost | 20880 | Financial Analysis - cost per acre foot
Owner's direct expense, 10% of direct capital cost | 42282.2667 | Equivalent Annual Cost (4% bond financed) | 67813.8132
Construction Overhead, 15% of direct capital cost | 63423.4 | Product Water, acre - feet | 25000
Interest During Construction (1/2 of period 6% rate) | 12684.68 | Equivalent annual cost per acre foot | 2.7126
Indirect Capital Costs | 139270.3467
Sources: VTE Geothermal Desalination Pilot Project data and estimates
Capital Cost | 562093.0133
15 Effect VTE Desalination Cost Estimate 5 MGD
Annual O&M costs Recharge (2009) | 31336 | Direct Capital Costs (adjusted to 2013)
Annual O&M costs Wellfield (2009) | 0 | Cooling Blowdown or Seawater Distillation Plant (2013) | 25369589.3258
|  | Working Capital (2 months of O&M costs) | 1003579.1306
Financial Analysis - cost per acre foot |  | Direct Capital Costs (adjusted to 2011) | 26373168.4564
Equivalent Annual Cost | 63726.6264
Product Water, acre - feet | 25000 | Indirect Capital Costs
Equivalent annual cost per acre foot | 2.5491 | Freight and Insurance, 5% of direct capital cost | 1318658.4228
|  | Owner's direct expense, 10% of direct capital cost | 2637316.8456
Sources: VTE Geothermal Desalination Pilot Project data and estimates |  | Construction Overhead, 15% of direct capital cost | 3955975.2685
|  | Interest During Construction (1/2 of period 6% rate) | 791195.0537
Desalination Costs |  | Indirect Capital Costs | 8703145.5906
Direct Capital Costs (original sources)
Ultrafiltration Plant (2001) | 0 | Capital Cost | 35076314.047
Source Water Development (2009) | 0
Recharge Facilities (2009) | 0 | Annual O&M costs Steam (2013) | 0
Cooling Blowdown or Seawater Distillation Plant (2009) | 28000000 | Annual O&M costs Distillation (2013) | 6021474.7835
Mitigation Costs (reduced flow from drains 2009) | 0
Product Water Distribution (2009) | 0 | Financial Analysis - cost per acre foot
Working Capital (2 months of O&M costs) | 193889.3333 | Equivalent Annual Cost (4% bond financed) | 8042318.8164
Direct Capital Costs (old) | 28193889.3333 | Product Water, acre - feet | 5000
|  | Equivalent annual cost per acre foot | 1608.4638
Indirect Capital Costs
Freight and Insurance, 5% of direct capital cost | 1400000
Owner's direct expense, 10% of direct capital cost | 2819388.9333 | Blended Water Cost (best TDS case)
Construction Overhead, 15% of direct capital cost | 4229083.4 | Direct Capital Costs (adjusted to 2013)
Interest During Construction (1/2 of period 6% rate) | 845816.68 | Ultrafiltration/Microfiltration Plant (2003) | 0
Indirect Capital Costs | 9294289.0133 | Source Water Development (2013) | 16841203.736
|  | Recharge Facilities (2013) | 222163.2
Capital Cost | 37488178.3467 | Seawater Distillation Plants (2013) | 25369589.3258
|  | Mitigation Costs (reduced flow from drains 2013) | 0
Annual O&M costs Nonofiltration (2001) | 0 | Product Water Distribution (2013) | 331968
Annual O&M costs Distillation (2009) | 1163336 | Working Capital (2 months of O&M costs) | 209076.7093
|  | Direct Capital Costs (adjusted to 2013) | 42974000.9711
Financial Analysis - cost per acre foot
Equivalent Annual Cost | 3323389.8181 | Indirect Capital Costs
Product Water, acre - feet | 5000 | Freight and Insurance, 5% of direct capital cost | 2148700.0486
Equivalent annual cost per acre foot | 664.678 | Owner's direct expense, 10% of direct capital cost | 4297400.0971
|  | Construction Overhead, 15% of direct capital cost | 6446100.1457
|  | Interest During Construction (1/2 of period 6% rate) | 1289220.0291
Blended Water Cost (best TDS case) |  | Indirect Capital Costs | 14181420.3205
Direct Capital Costs (original sources)
Ultrafiltration/Microfiltration Plant (2001) | 0 | Capital Cost | 57155421.2916
Source Water Development (2009) | 15828199
Recharge Facilities (2009) | 208800 | Annual O&M costs Wellfield (2013) | 1274051.688
Seawater Distillation Plants (2009) | 28000000 | Annual O&M costs Recharge (2013) | 16670.752
Mitigation Costs (reduced flow from drains 2009) | 0 | Annual O&M costs Distillation (2013) | 6021474.7835
Product Water Distribution (2009) | 312000
Working Capital (2 months of O&M costs) | 196500.6667 | Financial Analysis - cost per acre foot
Direct Capital Costs (old) | 44545499.6667 | Equivalent Annual Cost (4% bond financed) | 10605080.0479
|  | Product Water, acre - feet | 17000
Indirect Capital Costs |  | Equivalent annual cost per acre foot | 623.8282
Freight and Insurance, 5% of direct capital cost | 2217449.95
Owner's direct expense, 10% of direct capital cost | 4454549.9667
Construction Overhead, 15% of direct capital cost | 6681824.95
Interest During Construction (1/2 of period 6% rate) | 1336364.99
Indirect Capital Costs | 14690189.8567
Capital Cost | 59235689.5233
Annual O&M costs Wellfield (2009) | 1197417
Annual O&M costs Recharge (2009) | 15668
Annual O&M costs Distillation (2009) | 1163336
Financial Analysis - cost per acre foot
Equivalent Annual Cost | 5789412.8797
Product Water, acre - feet | 17000
Equivalent annual cost per acre foot | 340.5537

## IID Water Rate Calculator
Enter IID industrial water requirement | 16802.0351 | AFY | Remaining |  | Cost |  | IID Interim Water Supply Policy 2012 rate schedule
Water supply increment cost level 1 | 500 | AFY | 16302.0351 | AFY | 161875 | per year | Demand (AFY) | IID Reservation Fee | IID Development Fee
Water supply increment cost level 2 | 500 | AFY | 15802.0351 | AFY | 227915 | per year | 0-500 | 64.75 | 259
Water supply increment cost level 3 | 1500 | AFY | 14302.0351 | AFY | 858570 | per year | 501-1000 | 91.17 | 364.66
Water supply increment cost level 4 | 14302.0351 | AFY | 0 |  | 10112253.9388 | per year | 1001-2500 | 114.48 | 457.9
Total Annual Cost |  |  |  |  | 11360613.9388 | per year | 2501-5000 | 141.41 | 565.64